### CENWP-OP-B                                                                                                                         October 22, 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 42 of 2007, which covers the period from 14 through 20 October 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 82.5 to 137.0 kcfs.  Daily average project tailwater elevation ranged from 8.3’ to 12.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.9’ to 76.1’ msl.  Daily average river temperature ranged from 58° to 61°F.  Secchi disk measurements ranged from 6.0 to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.2 to 1.4 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service for turbine rehab since 04 June 2007.

    - Unit 8 has remained out of service for turbine rehab since 12 September 2006.

    - Unit 11went out of service at 0303 on 15 October for exciter replacement.

    - Unit 14 has remained out of service since 13 August for re-wedge and FGE modifications.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  No AWS closures this week.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  No dewatering and fish salvage activities occurred this week.

- RESEARCH

  - CRITFC.  Normal sampling operations continue.

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.

  - PSMFC Smolt Monitoring.  No fallbacks.  GBT concluded.  415 juvenile shad collected for researchers.

  - Univ. of Idaho.  Received 55 juvenile shad from the SMF this week.

  - USGS shad.  Received 360 juvenile shad from the SMF this week.

  - WDFW Fish Counting.  Daily visual counting continues at Bradford Island and Washington Shore.  Video monitoring at Cascades Island began on 1 October.

- FISHWAYS

  - Project biologists inspected daily from 14 through 20 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 10/16-20 | B-branch diff. | Reading <1.0’> | System in manual | Operators adjusted. |  |
| 10/16-18, 20 | B-branch entrance | S. gate incorrect position for TW | System in manual | Operators adjusted. |  |
| 10/17 | ITS & DSM1 | S gate closed | Workers attempt removal of lifting beam | S gate open at 1445 on 10/17 |  |
| CASCADES ISLAND |  |  |  |  |  |
| 10/16, 20 | UMT gauge | Reading >1.0’ | Unknown. | No action taken. |  |
| 10/17-20 | CI diff. | Reading<1.0’> | System in manual | Operators adjusted. |  |
| 10/16-18, 20 | CI entrance | N. gate incorrect position for TW | System in manual | Operators adjusted. |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Winter maintenance item. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 10/16-17, 20 | Weir 67 | Gauge > 1.0’ | UMT OOS and high forebay | No action taken |  |
| All week | DSM2 Airburst | Screens 3, 6 and 9 not consistent. | Bad controls. | Will replace during winter maintenance. |  |
| All week | DSM2 PLC | Not functioning at DSM2 |  | Repairs won’t be made until Dec/Jan |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

    - PH1 orifices in Units 1-9 were closed on 17 October at 1026 in preparation for closing the ITS and DSM1.  Unit 10 orifices and the South gate were closed at 1229.  This was necessary to allow workers to attempt to remove the lifting beam that got stuck under water.  The South gate was opened at 1445, and all PH1 orifice valves were opened at 1500 on 17 October.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 10/14 | 61.4 | 61.2 |
| 10/15 | 61.1 | 60.8 |
| 10/16 | 60.8 | 60.4 |
| 10/17 | 60.5 | 60.1 |
| 10/18 | 59.9 | 59.6 |
| 10/19 | 59.3 | 58.8 |
| 10/20 | 59.0 | 58.1 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 20 October.

    - B-Branch and Cascades Island are in manual.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - DSM1 continues to run south.  All available orifices are open.

    - The UMT remains closed.  Cascades Island exit remains open.

  - Juvenile Fishways.

    - DSM2 PLC is OOS.  Estimated time of repair is December or January.

    - SMF hydrocannons resumed operation on 04 October.

  - Lamprey Fishways.

    - All lamprey passage structures remain in service.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Plans to install three automated gates.  Optional items include sloping the floor and removing the DSM wall.

  - Bradford Island clean-up.  Removal of contaminated sediment currently underway.

  - PH2 VBS mods.  Unit 14 is currently OOS.  U18 will follow.  U17 VBS monitoring equipment will be installed at this time as well.

  - TIE crane.  The TIE crane boom repair is awaiting funding.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.

JAMES R. MAHAR, P.E.

Operations Manager