### CENWP-OP-B                                                                                                                         November 14, 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 45 of 2007, which covers the period from 04 through 10 November 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 80.5 to 123.0 kcfs.  Daily average project tailwater elevation ranged from 7.4’ to 11.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.7’ msl.  Daily average river temperature ranged from 54° to 55°F.  Secchi disk measurements were 7.0’ every day.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill was 1.1 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 0 was out of service from 0014 on 5 November until 1437 on 6 November for annual maintenance.

    - Unit 1 has remained out of service since 23 October due to governor trouble.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 9 was out of service from 0001 until 1736 on 7 November for annual maintenance.

    - Unit 11 returned to service at 1645 on 8 November.

    - Unit 12 was out of service from 1449 until 1625 on 8 November due to loss of speed control.

    - Unit 14 has remained out of service since 13 August for re-wedge and FGE modifications.

    - Unit 18 was out of service from 1000 until 1055 on 30 October for STS inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 0810 until 0912 on 7 November due to a loose wire on metering.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting period:

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  No dewatering or salvage activities took place this reporting week.

- RESEARCH

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.

  - WDFW Fish Counting.  Daily video counting continues at Bradford Island and Washington Shore.  Video monitoring continues at Cascades Island.

- FISHWAYS

  - Project biologists inspected daily from 04 through 10 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| All week | B-branch diffusers | FG 3-27 incorrect position for TW | A lot of water exiting FG3-28 | See 4.2.6 or 4.5.3 |  |
| 11/7 | B-branch entrance | S. gate incorrect position for TW | System in manual | Operators adjusted |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| CASCADES ISLAND |  |  |  |  |  |
| 11/5 | CI differential | <1.5’ | System in manual | FV4-4 adjusted |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Winter maintenance item. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| All week | DSM2 Airburst | Screens 3, 6 and 9 not consistent. | Bad controls. | Will replace during winter maintenance. |  |
| 11/5-7 | Weir 67 | Reading <1.0’> | UMT closed. | No action taken. |  |
| 11/5 | S. monolith | SUE closing | Sensor trouble at 10’ TW | System autocorrects. Put in manual. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - The Bradford Island temperature sensor is malfunctioning and is awaiting repair.  Temperatures generally track those of WS.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 11/4 | 56.1 | See 4.3.1 |
| 11/5 | 55.9 |  |
| 11/6 | 55.4 |  |
| 11/7 | 55.4 |  |
| 11/8 | 55.6 |  |
| 11/9 | 55.3 |  |
| 11/10 | 55.2 |  |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was not checked this week.

    - B-Branch and Cascades Island are in manual.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - DSM1 continues to run south.  All available orifices are open.

    - The UMT remains closed.  Cascades Island exit remains open.

    - WS Monolith gates were put to manual on 6 November, due to TW elevation sensor issues.

  - Juvenile Fishways.

    - DSM2 PLC is OOS.  Estimated time of repair is December or January.

    - SMF hydrocannons resumed operation on 04 October.

    - The SMF remains in bypass.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Plans to install three automated gates.  Optional items include sloping the floor and removing the DSM wall.

  - Bradford Island clean-up.  Removal of contaminated sediment currently underway.

  - PH2 VBS mods.  Unit 14 is currently OOS.  U18 will follow.  U17 VBS monitoring equipment will be installed at this time as well.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 7 November requests a tailwater operation for chum spawning, effective 9 November until further notice.  The Project is asked to maintain a hard constraint TW elevation of 11.3’ to 11.7’ 24 hours a day, with a target of 11.5’.  The official Project TW gauge is located at river mile 144.5, on the Oregon side.  This request was coordinated with TMT.

  - A teletype sent on 8 November modifies the chum spawning teletype (see 7.1) by including the following language in the event flows are too high to maintain desired TW elevations:

    - Hard constraint minimum TW elevation of 11.3’ during all hours.

    - Between 0700 and 1900, hard constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - Between 1900 and 0700, soft constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - If inflows exceed the 11.5’ TW, additional water should be shaped into the night hours, preferably in one four hour or less event.

  - The draft 2008 FPP will be out by early December.

JAMES R. MAHAR, P.E.

Operations Manager