### CENWP-OP-B                                                                                                                         November 19, 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 46 of 2007, which covers the period from 11 through 17 November 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 118.9 to 130.6 kcfs.  Daily average project tailwater elevation was 11.5’ msl.  Daily average powerhouse forebay elevation ranged from 74.4’ to 76.3’ msl.  Daily average river temperature ranged from 52° to 54°F.  Secchi disk measurements ranged from 4.0’ to 7.0.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill was 1.1 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 1 has remained out of service since 23 October due to governor trouble.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 14 has remained out of service since 13 August for re-wedge and FGE modifications.

    - Unit 15 was out of service from 1242 on 13 November until 1427 on 14 November for PPT (electrical) work.

    - Unit 16 was out of service from 0353 until 1238 on 13 November for exciter follow-up work.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV1-1 was closed from 1252 until 1330 on 17 November for cleaning.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  No dewatering or salvage activities took place this reporting week.

- RESEARCH

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.

  - WDFW Fish Counting.  Daily video counting continues at Bradford Island, Washington Shore, and Cascades Island.

- FISHWAYS

  - Project biologists inspected daily from 12 through 17 November.  NOAA inspected on 16 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 11/11 | Bonneville | Inspection not done. |  |  |  |
| 11/13 | Collection channel | South entrance <1.0 | Unknown | Operator adjusted |  |
| All week | B-branch diffusers | FG 3-27 incorrect position for TW | A lot of water exiting FG3-28 | See 4.2.6 or 4.5.3 |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Winter maintenance item. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| All week | DSM2 Airburst | Screens 3, 6 and 9 not consistent. | Bad controls. | Will replace during winter maintenance. |  |
| 11/13, 11/15-17 | Weir 67 | Reading > 1.0’ | UMT closed. | No action taken. |  |
| All week | S. monolith | SUE closing | Sensor trouble at 10’ TW | System autocorrects. Put in manual. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - The Bradford Island temperature sensor is malfunctioning and is awaiting repair.  Temperatures generally track those of WS.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 11/11 | 54.8 | See 4.3.1 |
| 11/12 | 54.3 |  |
| 11/13 | 53.9 |  |
| 11/14 | 53.4 |  |
| 11/15 | 53.0 |  |
| 11/16 | 53.2 |  |
| 11/17 | 53.2 |  |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 17 November.

    - B-Branch and Cascades Island are in manual.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - DSM1 continues to run south.  All available orifices are open.

    - The UMT remains closed.  Cascades Island exit remains open.

    - WS Monolith gates were put to manual on 6 November, due to TW elevation sensor issues.

  - Juvenile Fishways.

    - DSM2 PLC is OOS.  Estimated time of repair is December or January.

    - SMF hydrocannons resumed operation on 04 October.

    - The SMF remains in bypass.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Plans to install three automated gates.  Optional items include sloping the floor and removing the DSM wall.

  - Bradford Island clean-up.  Removal of contaminated sediment has concluded.

  - PH2 VBS mods.  Unit 14 is currently OOS.  U18 will follow.  U17 VBS monitoring equipment will be installed at this time as well.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - TIE scrapping.  Six TIEs are currently being scrapped and removed from the project.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 7 November requests a tailwater operation for chum spawning, effective 9 November until further notice.  The Project is asked to maintain a hard constraint TW elevation of 11.3’ to 11.7’ 24 hours a day, with a target of 11.5’.  The official Project TW gauge is located at river mile 144.5, on the Oregon side.  This request was coordinated with TMT.

  - A teletype sent on 8 November modifies the chum spawning teletype (see 7.1) by including the following language in the event flows are too high to maintain desired TW elevations:

    - Hard constraint minimum TW elevation of 11.3’ during all hours.

    - Between 0700 and 1900, hard constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - Between 1900 and 0700, soft constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - If inflows exceed the 11.5’ TW, additional water should be shaped into the night hours, preferably in one four hour or less event.

  - A teletype sent on 14 November details a temporary change in unit priority from 0000 19 November to 2400 20 November due to dive operations in the forebay.  Unit priority will shift from B2 to B1, as necessary, while 2 main units and both fish units at B2 remain in service.  To maintain flow and tailwater (see 7.2), units may run outside of 1% efficiency as needed.

  - A teletype sent on 15 November replaces the 14 November teletype (see 7.3).   From 0000 19 November to 2400 20 November due to dive operations in the B2 forebay, unit priority will shift from B2 to B1.  Both fish units and two main units will remain in service at B2.  To maintain flow and tailwater (see 7.2), units may run outside of 1% efficiency as needed, and a third main unit may be required at B2 to in order to maintain tailwater.

  - A teletype sent on 16 November, effective immediately until 1800 on 17 November, approves a possible forebay exceedence at Bonneville to control the high amount of water in the river and maintain tailwater for chum spawning (see 7.2).  The exceedence may be above the 76.5’, and may go as high as 77.0’.

  - The draft 2008 FPP will be out by early December.

JAMES R. MAHAR, P.E.

Operations Manager