### CENWP-OP-B                                                                                                                         December 12, 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 49 of 2007, which covers the period from 2 December through 8 December 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 110.9 to 169.0 kcfs.  Daily average project tailwater ranged from 12.3’ to 16.9’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 75.1’ msl.  Daily average river temperature ranged from 45° to 46°F.  Secchi disk measurements ranged from 1.0’ to 6.0.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.1 to 1.4 kcfs.

  - Unit Operation.   Powerhouse 2 is the priority powerhouse.

    - Unit 1 has remained out of service since 23 October due to governor trouble.

    - Unit 2 went out of service from 1030 until 1656 on 04 December due to slip ring holder problems.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 went out of service from 0747 until 1403 on 03 December due to STS ‘A’ power cord disconnect.

    - Unit 14 has remained out of service since 13 August for re-wedge and FGE modifications.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 18 went out of service at 0743 on 03 December for FGE modifications and 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Unit F2 went out of service at 0106 on 03 December for exciter replacement.  PH2 collection channel is set for single unit operations per FPP.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV1-1 was closed from 1517 until 1620 on 04 December for cleaning.  FV 1-1 was also closed from 2040 on 04 December until 0500 on 05 December, and 1826 on 08 December until 0508 on 09 December to float trash.

    - FV 3-7 was closed from 1604 until 1704 on 03 December, and from 1012 until 1354 on 04 December for cleaning.

    - FV 3-9 was closed from 1604 until 1704 on 03 December and from 1012 until 1354 on 04 December for cleaning

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.

    - Seven sturgeon were removed from Unit 18 draft tube on 5 December.  All were released at the Hamilton Island boat launch in good condition.

- RESEARCH

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility continues.

  - WDFW Fish Counting.  Video counting continues at Bradford Island, Cascades Island and WA Shore.

- FISHWAYS

  - Project biologists inspected on 3, 5-7 December.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 12/3, 6 | A & B-branch weirs, BI weir | <1.0’ | Excessive debris at FV 3-9 | Riggers cleaned |  |
| 12/7 | B-branch diffusers | FG 3-25, 26 open | System in manual | Operator adjusted |  |
| All week | B-branch diffusers | FG 3-27 incorrect position for TW | A lot of water exiting FG3-28 | See 4.2.6 or 4.5.3 |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Winter maintenance item. |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| WASHINGTON SHORE |  |  |  |  |  |
| 12/5 | Weir 67 | Reading > 1.0’ | UMT closed. | No action taken. |  |
| 12/3, 5, 6 | DSM2 | Channel elevation <62.4’ | Low FB, multiple orifices OOS | See 4.2.8 or 4.6.4 |  |
| 12/5, 6 | PH2 monoliths | Differential <1.0’ | F2 OOS | Operators adjusted. |  |
| All week | DSM2 Airburst | Screens 3, 6 and 9 not consistent. | Bad controls. | Will replace during winter maintenance. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

    - DSM2 channel elevation has been running <62.4’ when the forebay is low.  This is due to many orifices being unavailable.  All four F2 orifices have been opened, and U14 is expected to be back in service next week.

  - Fishway Temperatures.  Temperatures are only taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 06 December.

    - B-Branch and Cascades Island are in manual.

    - FG3-27 is open regardless of TW.  This is to reduce water and pressure from FG3-28.  The excess water may be due to FV4-3 not operating as it should.  Maintenance will repair FV4-3 this winter.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - DSM1 continues to run south.  All available orifices are open.

    - The UMT remains closed.  Cascades Island exit remains open.

    - WS Monolith gates remain in manual due to TW elevation sensor issues.

    - PH2 FOG stab plates are installed as of 03 December due to Fish Unit 2 outage.

  - Juvenile Fishways.

    - DSM2 PLC is OOS.  Estimated time of repair is December or January.

    - SMF hydrocannons are scheduled to be winterized on 10 December.

    - The SMF remains in bypass.

    - Unit F2 manual orifice valves were opened at 2059 on 05 December to help maintain DSM2 level.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  Unit 14 and 18 are currently OOS.  U17 VBS monitoring equipment will be installed at this time as well.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - TIE scrapping.  Six TIEs are currently being scrapped and removed from the project, scheduled to conclude on 14 December.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 7 November requests a tailwater operation for chum spawning, effective 9 November until further notice.  The Project is asked to maintain a hard constraint TW elevation of 11.3’ to 11.7’ 24 hours a day, with a target of 11.5’.  The official Project TW gauge is located at river mile 144.5, on the Oregon side.  This request was coordinated with TMT.

  - A teletype sent on 29 November modifies the chum spawning teletype (see 7.1) by changing the following language in the event flows are too high to maintain desired TW elevations:

    - Hard constraint minimum TW elevation of 11.3’ during all hours.

    - Between 0600 and 1800, hard constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - Between 1800 and 0600, soft constraint TW elevation 11.3’ to 11.7’, with a target of 11.5’.

    - If there is a need to pass water in excess of the tailwater constraint, the project is authorized between the hours of 1800 and 0600 to raise the tailwater up to 13.0’ for up to 8 hours.

    - If the above step is not enough to pass excess water, the project is authorized between the hours of 2200-0400 to raise the tailwater up to 15.0’ for 4 hours.

  - A teletype sent on 04 December replaces the chum spawning teletype (see 7.2) effective immediately until further notice, in an effort to gain control of the lower river and return to the 11.3’ to 11.7’ daytime operations.  The project is asked to maintain outflows as high as possible around the clock, up to a full powerhouse.  To avoid emptying the pool, the project can back off flows from 1800 to 0600 hours.  The project is asked to maintain a hard constraint minimum TW elevation of 11.3’ during all hours.

  - A teletype sent on 06 December states that the project can operate the B2CC beginning immediately through 10 December in an attempt to clean trash from the B2CC.

  - The draft 2008 FPP will be out by early December.

  - The winter maintenance schedule is available from Project Fisheries.

    - Bradford Island is scheduled to go to orifice flow on 14 December.  It will be dewatered on 17 December.

    - DSM2 and the two mile pipe will be dewatered on 19 December.

    - DSM1 will be dewatered on 20 December.

JAMES R. MAHAR, P.E.

Operations Manager