### CENWP-OP-B                                                                                                                         January 16, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 02 of 2008, which covers the period from 06 January through 12 January 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 145.5 to 175.6 kcfs.  Daily average project tailwater ranged from 14.3’ to 16.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.3’ msl.  Daily average river temperature ranged from 40° to 41°F.  Secchi disk measurements ranged from 6.0’ to 7.0.’

  - Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill ranged from 0.5 to 0.6 kcfs.

  - Unit Operation.   Powerhouse 2 is the priority powerhouse.

    - Unit 1 has remained out of service since 23 October due to governor trouble.

    - Unit 4 was out of service from 0120 until 0746 on 11 January due to ground search.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 9 was out of service from 1221 until 1346 on 11 January to replace failed digital governor.

    - Unit 10 was out of service from 0725 on 10 January until 1151 on 11 January due to breaker failure.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Unit F2 returned to service at 1244 on 11 January.  It had been out of service since 03 December for exciter replacement.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

    - FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | All screens were pulled for winter maintenance. |

  - Dewatering and Fish Salvage.

    - B-branch was dewatered below tailwater on 07 January.  In an effort minimize the number of fish in the ladder, particularly sturgeon, seal bomb usage was halted as a precaution two days prior to dropping bulkheads on 02 January.  Each diffuser was also opened sequentially (top to bottom) in an effort to drive any fish out.  No fish were present in the ladder.

- RESEARCH

  - WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.

- FISHWAYS

  - Project biologists inspected on 07-09 January.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES- OOS for the winter season |  |  |  |  |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Winter maintenance item. |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| WASHINGTON SHORE |  |  |  |  |  |
| 1/7 | FG6-12 | Incorrect position for TW | System in manual | Operators adjusted. |  |
| 1/7-8 | Weir 67 | Reading > 1.0’ | UMT closed. | No action taken. |  |
| 1/8 | PH2 monoliths | Differential <1.0’ | F2 OOS | Operators adjusted. |  |
| All week | WS velocity | Meter reading <1.0 | Unknown- may be related to the low differential. | Fisheries will monitor. |  |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 09 January.

    - BI was dewatered on 17 December.

    - Cascades Island fishway PLC is in manual.

    - The UMT remains closed.  Cascades Island exit remains open.

    - PH2 FOG stab plates are installed as of 03 December due to Fish Unit 2 outage.

    - The AFF was dewatered on 31 December.

  - Juvenile Fishways.

    - DSM 1 and 2 remain dewatered.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  Unit 18 is currently OOS.  U17 VBS monitoring equipment will be installed during this winter maintenance period.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.

  - A teletype sent on 02 January requests a change in PH1 unit priority.  Unit 2 is to be operated on a last on, first off basis for approximately one month, due to an undiagnosed problem with the unit.

JAMES R. MAHAR, P.E.

Operations Manager