### CENWP-OP-B                                                                                                                         January 22, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 03 of 2008, which covers the period from 13 January through 19 January 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 128.1 to 173.9 kcfs.  Daily average project tailwater ranged from 13.7’ to 15.8’ msl.  Daily average powerhouse forebay elevation ranged from 74.0’ to 75.0’ msl.  Daily average river temperature ranged from 39° to 40°F.  Secchi disk measurements ranged from 5.0’ to 7.0.’

  - Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill ranged from 0.5 to 0.6 kcfs.

  - Unit Operation.   Powerhouse 2 is the priority powerhouse.

    - Unit 1 has remained out of service since 23 October due to governor trouble.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Unit F1 went out of service at 2058 on 13 January for exciter replacement.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

    - FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | All screens were pulled for winter maintenance. |

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.

  - Fish Field Unit.  Pinniped observations began on 11 January.

  - WDFW/ODFW Sea lion hazing.  Hazing from boats began on 12 December.

- FISHWAYS

  - Project biologists inspected on 14, 16-17 January.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES- OOS for the winter season |  |  |  |  |  |
| CASCADES ISLAND |  |  |  |  |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| WASHINGTON SHORE |  |  |  |  |  |
| 1/14, 17 | Weir 67 | Reading > 1.0’ | UMT closed. | No action taken. |  |
| 1/14 | PH2 monoliths | Differential <1.0’ | F2 OOS | Operators adjusted. |  |
| All week | WS velocity | Meter reading <1.0 | Unknown- may be related to the low differential. | Fisheries will monitor. |  |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 17 January.

    - BI was dewatered on 17 December.

    - Cascades Island fishway PLC is in manual.

    - The UMT remains closed.  Cascades Island exit remains open.

    - PH2 FOG stab plates are installed as of 03 December due to Fish Unit outages.

    - The AFF was dewatered on 31 December.

    - The Washington shore exit gate was closed from 1756 until 1940 on 14 January (see 7.3).

  - Juvenile Fishways.

    - DSM 1 and 2 remain dewatered.

    - The DSM 2 two mile pipe was inspected on 15 January.  No problems were noted.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  Unit 18 is currently OOS.  U17 VBS monitoring equipment will be installed during this winter maintenance period.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - BGS.  Installation of the BGS is scheduled to begin next week.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.

  - A teletype sent on 02 January requests a change in PH1 unit priority.  Unit 2 is to be operated on a last on, first off basis for approximately one month, due to an undiagnosed problem with the unit.

  - The Washington shore exit gate was closed from 1756 until 1940 on 14 January to perform an emergency inspection of the ladder.  The Project had reason to believe that there was a potential suicide victim in the Washington shore fishway.  Nothing was found and the ladder was put back in normal operations upon conclusion.  Project biologists were present during this operation.

JAMES R. MAHAR, P.E.

Operations Manager