### CENWP-OP-B                                                                                                                         February 19, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 07 of 2008, which covers the period from 10 through 16 February 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 106.7 to 182.5 kcfs.  Daily average project tailwater ranged from 12.1’ to 16.0’ msl.  Daily average powerhouse forebay elevation ranged from 73.8’ to 75.4’ msl.  Daily average river temperature ranged from 37° to 38°F.  Secchi disk measurements ranged from 4.0 to 6.0.’

  - Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill was 0.6 kcfs.

  - Unit Operation.   Powerhouse 2 is the priority powerhouse.

    - Unit 1 returned to service at 1351 on 14 February.  It had been out of service since 23 October due to governor trouble.

    - Unit 1 was out of service from 2002 on 14 February until 0827 on 15 February due to water in turbine bearing oil.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 12 was out of service from 1037 until 1410 on 13 February, 1054 until 1503 on 14 February, 1055 until 1456 on 15 February, and 1055 until 1447 on 16 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 13 was out of service from 1033 until 1414 on 13 February, 1034 until 1504 on 14 February, 1025 until 1506 on 15 February, and 1055 until 1456 on 16 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 13 went out of service at 1516 on 16 February due to possible water in the turbine bearing oil.

    - Unit 14 was out of service from 1026 until 1425 on 13 February, 1022 until 1516 on 14 February, 1054 until 1501 on 15 February, and 1055 until 1456 on 16 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 was out of service from 1016 until 1425 on 13 February, 1009 until 1517 on 14 February, 1012 until 1519 on 15 February, and 1055 until 1456 on 16 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

    - FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | All screens were pulled for winter maintenance. |

  - Dewatering and Fish Salvage.

    - Fish were salvaged from Unit 1 tail logs on 13 February.  Five sturgeon, one unclipped steelhead, 14 sculpin, one sucker, one juvenile Chinook, and four crayfish were all released in good condition.

- RESEARCH

  - WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.

  - Fish Field Unit.  Pinniped observations continue.

  - Fish Field Unit. Sea lion scat collections continue.

  - WDFW/ODFW Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 11, 13-14 February.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES- OOS for the winter season |  |  |  |  |  |
| CASCADES ISLAND |  |  |  |  |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| WASHINGTON SHORE |  |  |  |  |  |
| 2/11 | PH2 Diffusers | Incorrect position for TW | In manual | Operators adjusted. |  |
| 2/11, 14 | Weir 38 | Differential <1.0’ | Weir 50 add-in closed due to winterization. | No action taken. |  |
| 2/13 | Weir 67 | Differential >1.0’ | UMT closed | No action taken. |  |
| 2/14 | CI entrance | Differential <1.0’ | In manual | Operators adjusted. |  |
| 2/14 | CI diffusers | Incorrect position for TW | In manual | Operators adjusted. |  |
| 2/14 | CI entrance gates | Incorrect position for TW | In manual | Operators adjusted. |  |
| 2/14 | WS velocity | Meter reading <1.0 | Unknown- may be related to the low differential. | Fisheries will monitor. |  |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  It is only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 14 February.

    - BI was dewatered on 17 December.

    - Cascades Island fishway PLC is in manual.

    - The UMT remains closed.  Cascades Island exit remains open.

    - PH2 FOG stab plates are installed as of 03 December due to Fish Unit outages.  Stab plates will remain installed until new sea lion barriers are fabricated.

    - The AFF was dewatered on 31 December.

    - SLEDS are installed at all PH2 fishway entrances and Cascades Island.

  - Juvenile Fishways.

    - DSM 1 and 2 remain dewatered.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  Unit 18 is currently OOS.  U17 VBS monitoring equipment will be installed during this winter maintenance period.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - BGS.  Installation of the BGS continues.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.

  - A teletype sent on 06 February requests the following special operations while the behavioral guidance structure is being installed in the PH2 forebay:

    - This operation is to occur on Thursdays and Fridays from 1100-1500 each day, February 8, 14 & 15, 21 & 22

    - The project will operate only two main units plus the fish units at PH2, with the rest of the outflow going through PH1.  The location of the two operating units will be determined by the location of the dive.

    - PH2 will return to normal operations over the next two hours, once the dive is completed.  BPA will attempt to keep low flows even outside the four hour operational period.

    - The minimum tailwater of 11.5’ will be maintained (see 7.1).

    - The project is authorized outside the standard unit operating priority as described in the Fish Passage Plan during this operation, and when needed to setup and return to normal operation.

    - The dive coordinators for Advanced American diving will contact the project, who will contact BPA, if the dives are completed earlier than specified.

  - A teletype sent on 11 February changes BON unit priority, beginning now until further notice.  PH1 is to be the priority powerhouse, which overrides Table BON-5 in the 2007 Fish Passage Plan, to facilitate the installation of the BGS in the PH2 forebay.  When low flows are not required at PH2, it is requested that a minimum of four units be operated at PH2.

  - A teletype sent on 11 February requests additional dates be added to the teletype sent on 06 February (see 7.2):  Friday, 15 February.  All other special operations remain the same.

  - A teletype sent on 11 February requests the lowest flows practical from PH2 on the following Tuesdays and Wednesday: February 12-13, February 19-20, and February 27-28.  The hours on Tuesdays are from 0800-1600, and on Wednesdays the hours are 0800-1100 and 1500-1600.  The minimum tailwater of 11.5’ (see7.1) will be maintained.  This request is a soft constraint.

  - A teletype sent on 15 February requests Spillbay 1 to be closed on 19 February at 0630 until normal opening time on 20 February.  This is necessary to perform a hydrosurvey in front of Spillbays 1 and 2.  This operation temporarily suspends the requirement for bays 1 and 18 to be open as stated in the 2007 Fish Passage Plan on page BON-14.

  - A teletype sent on 15 February requests additional dates be added to the teletype sent on 06 February (see 7.2 and 7.4):  Saturday, 16 February.  All other special operations remain the same.

JAMES R. MAHAR, P.E.

Operations Manager