### CENWP-OP-B                                                                                                                         February 27, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 08 of 2008, which covers the period from 17 through 23 February 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 126.3 to 174.6 kcfs.  Daily average project tailwater ranged from 11.9’ to 14.8’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 74.6’ msl.  Daily average river temperature ranged from 38° to 40°F.  Secchi disk measurements ranged from 4.0 to 6.0.’

  - Spill Bay 1, which supplies attraction flow for Cascades Island, is included in the spill pattern.  Daily average spill ranged from 0 to 0.6 kcfs.

    - Spill Bay 1 was placed on sill from 1905 on 18 February until 0600 on 20 February to facilitate the hydro survey and ROV inspection in front on Spill Bays 1 & 2 (see 7.6).

  - Unit Operation.   Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 was out of service from 1023 until 1636 on 20 February, 1018 until 1611 on 22 February, and 1010 until 1609 on 23 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 11 was out of service from 0637 until 1617 on 21 February to rake trash and to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 12 was out of service from 1023 until 1605 on 20 February, 0924 until 1617 on 21 February, and 1010 until 1609 on 23 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 13 returned to service at 1657 on 19 February.  It had been out of service since 16 February due to possible water in the turbine bearing oil.

    - Unit 13 was out of service from 1023 until 1608 on 20 February, 0927 until 1617 on 21 February, and 1018 until 1608 on 22 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 14 was out of service from 1018 until 1608 on 22 February and 1010 until 1609 on 23 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 was out of service from 1023 until 1604 on 20 February and 0934 until 1617 on 21 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 17 was out of service from 1035 until 1611 on 22 February to facilitate the BGS installation dive in the PH2 forebay.

    - Unit 17 went out of service at 0413 on 23 February for FGE modifications.

    - Unit 18 has remained out of service since 03 December for FGE modifications and 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Unit F2 was placed in standby from 0743 until 1022 on 19 February to facilitate the PH2 ROV inspection.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting period:

    - FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

    - FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

    - FV 5-3 and 5-4 were closed from 0637 until 1525 on 19 February for the Cascades Island ROV inspection.

    - FV 5-9 was closed from 1040 until 1525 on 19 February for the Cascades Island ROV inspection.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3-4, 11-18 | NA | NA | All screens were pulled for winter maintenance. |

  - Dewatering and Fish Salvage.

    - Fish were salvaged from Unit 18 tail logs on 21 February.  Two sculpin and 23 sturgeon were released in good condition.  Two sturgeon mortalities were observed.

- RESEARCH

  - WDFW Fish Counting.  Video counting continues at Cascades Island and WA Shore.

  - Fish Field Unit.  Pinniped observations continue.  The pinniped trap is now in place.

  - Fish Field Unit. Sea lion scat collections continue.

  - WDFW/ODFW Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 19-22 February.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES- OOS for the winter season |  |  |  |  |  |
| CASCADES ISLAND-no violations |  |  |  |  |  |
| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| WASHINGTON SHORE |  |  |  |  |  |
| 2/22 | PH2 Diffusers | Incorrect position for TW | In manual | Operators adjusted. |  |
| 2/19, 22 | Weir 38 | Differential <1.0’ | Weir 50 add-in closed due to winterization. | No action taken. |  |
| 2/20 | Weir 37 | Differential >1.0’ | Bleed off valve closed due to winterization. | No action taken. |  |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 07/08.  It is only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 22 February.

    - BI was dewatered on 17 December.

    - Cascades Island fishway PLC is in manual.

    - The UMT remains closed.  Cascades Island exit remains open.

    - PH2 FOG stab plates are installed as of 03 December due to Fish Unit outages.  Stab plates will remain installed until new sea lion barriers are fabricated.

    - The AFF was dewatered on 31 December.

    - SLEDS are installed at all PH2 fishway entrances and Cascades Island.

  - Juvenile Fishways.

    - DSM 1 and 2 remain dewatered.

  - Lamprey Fishways.  Winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  Unit 18 is currently OOS.  U17 VBS monitoring equipment will be installed during this winter maintenance period.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - BGS.  Installation of the BGS continues.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tail water as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.

  - A teletype sent on 06 February requests the following special operations while the behavioral guidance structure is being installed in the PH2 forebay:

    - This operation is to occur on Thursdays and Fridays from 1100-1500 each day, February 8, 14 & 15, 21 & 22

    - The project will operate only two main units plus the fish units at PH2, with the rest of the outflow going through PH1.  The location of the two operating units will be determined by the location of the dive.

    - PH2 will return to normal operations over the next two hours, once the dive is completed.  BPA will attempt to keep low flows even outside the four hour operational period.

    - The minimum tailwater of 11.5’ will be maintained (see 7.1).

    - The project is authorized outside the standard unit operating priority as described in the Fish Passage Plan during this operation, and when needed to setup and return to normal operation.

    - The dive coordinators for Advanced American diving will contact the project, who will contact BPA, if the dives are completed earlier than specified.

  - A teletype sent on 11 February changes BON unit priority, beginning now until further notice.  PH1 is to be the priority powerhouse, which overrides Table BON-5 in the 2007 Fish Passage Plan, to facilitate the installation of the BGS in the PH2 forebay.  When low flows are not required at PH2, it is requested that a minimum of four units be operated at PH2.

  - A teletype sent on 11 February requests additional dates be added to the teletype sent on 06 February (see 7.2):  Friday, 15 February.  All other special operations remain the same.

  - A teletype sent on 11 February requests the lowest flows practical from PH2 on the following Tuesdays and Wednesday: February 12-13, February 19-20, and February 27-28.  The hours on Tuesdays are from 0800-1600, and on Wednesdays the hours are 0800-1100 and 1500-1600.  The minimum tailwater of 11.5’ (see7.1) will be maintained.  This request is a soft constraint.

  - A teletype sent on 15 February requests Spill Bay 1 to be closed on 19 February at 0630 until normal opening time on 20 February.  This is necessary to perform a hydro survey in front of Spill Bays 1 and 2.  This operation temporarily suspends the requirement for bays 1 and 18 to be open as stated in the 2007 Fish Passage Plan on page BON-14.

  - A teletype sent on 15 February requests additional dates be added to the teletype sent on 06 February (see 7.2 and 7.4):  Saturday, 16 February.  All other special operations remain the same.

  - A teletype sent on 19 February requests additional dates and times be added to the teletype sent on 06 February (see 7.2, 7.4, and 7.7): 1100-1600 each day, on February 20, 21, 22, 23, 25, 27, 28, and 29.

  - During the ROV inspection on 19 February, large quantities of sturgeon were seen in the Cascades Island fishway entrance and downstream of Spill Bays 1 & 2.  The aggregation of sturgeon appears to be the 15’ debris pile identified in a previous hydro survey in front of Bay 2.

JAMES R. MAHAR, P.E.

Operations Manager