### CENWP-OP-B                                                                                                                         March 31, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 13 of 2008, which covers the period from 23 March through 29 March 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 121.4 to 187.4 kcfs.  Daily average project tailwater ranged from 12.2’ to 16.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.7’ to 75.4’ msl.  Daily average river temperature was 44°F.  Secchi disk measurements ranged from 5.0 to 6.9.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 1.1 to 1.4 kcfs.

    - Bay 1 went on sill at 1220 to accommodate the spillway dive operation.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 3 operated outside the 1% from 1354 until 1400 on 26 March to facilitate trash raking at U4.

    - Unit 5 operated outside the 1% from 1515 until 1536 on 25 March to facilitate trash raking at U6.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 10 operated outside the 1% from 1025 until 1038 on 25 March to facilitate trash raking at U9.

    - Unit 11 was out of service from 0609 until 1620 on 29 March to facilitate the BGS dive.

    - Unit 12 was out of service from 0621 until 1630 on 29 March to facilitate the BGS dive.

    - Unit 13 went out of service at 0413 on 27 March for exciter replacement work.

    - Unit 14 was operated at the low end of 1% at 1247 on 26 March to facilitate gatewell testing.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 has remained out of service since 05 March for FGE repairs in gatewell 16A.

    - Unit 17 returned to service at 1704 on 26 March.  Unit 17 was out of service from 0614 until 1658 on 29 March to facilitate the BGS dive.

    - Unit 18 was out of service from 1232 until 1642 on 28 March for packing adjustments.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 load was reduced to 5MW from 1308 until 1700 on 25 March and from 0717 until 1052 on 26 March to facilitate the FOG exclusion bar installation.  F1 was at reduced load from 0909 until 0932 on 28 March to facilitate the ROV inspection of SDE.

    - F2 load was reduced to 5MW from 1308 until 1700 on 25 March to facilitate the FOG exclusion bar installation.  F2 was out of service from 0200 on 26 March until 1249 on 27 March for servo repairs.  F2 was at reduced load from 0909 until 0938 on 28 March to facilitate the ROV inspection of SDE.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week.

    - FV4-3/4-4 from 1210 until 1530 on 27 March for the spillway erosion survey dive.

    - FV5-3/5-4 from 1250 until 1630 on 25 March and from 1225 until 1730 on 26 March for the spillway erosion survey dive.

  - STS/VBS Inspections.  The following STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 3/26 | 519 |  |
| 12 | 3/26 | 526 |  |
| 13 | 3/26 | 571 | B slot. 88 x 12 in. rip. Repaired |
| 14 | 3/26 | 585 | VBS inspected on 3/25. Fish in between perf plate and back of VBS and gaps in rubber seals. Engineering working on repairs. |
| 15 |  |  | OOS |
| 16 |  |  | OOS |
| 17 |  |  | OOS |
| 18 | 3/26 | 590 |  |

  - Dewatering and Fish Salvage. The following fish salvage activities occurred this reporting week.

    - 13 Sturgeon were recovered from the U16 tail logs on 27 March.

- RESEARCH

  - Battelle.  Monitoring with DIDSON acoustic camera and split-beam hydroacoustics near B2CC entrance to estimate the numbers and distribution of kelt sized targets.

  - Fish Field Unit.  Pinniped observation and scat collection continue.

  - NOAA- Gilbreath.  Juvenile fish releases in gatewell 14A began on 26 March.

  - PSMFC Smolt Monitoring. Index and condition sampling continues.

  - USDA Wildlife Services. Sea lion hazing from the powerhouses continues.

  - WDFW Fish Counting.  Video counting continues at Bradford Island and WA Shore.

  - WDFW/ODFW Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 23-25, 27-29 March.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 3/25, 28-29 | B-branch diff. | Incorrect position | System in manual | Ops adjusted |  |
| 3/27 | FV4-3/4-4 | Closed | Spillway dive | In criteria by 1530 |  |
| 3/27 | B-branch ent. | Differential <1.0’ | Spillway dive | In criteria at 1530 |  |
| All week | WG 64 | Incorrect position | Brake seized | Waiting on parts to come in. |  |
| CASCADES ISLAND |  |  |  |  |  |
| 3/25-26 | FV5-3/5-4 | Closed | Spillway dive | In criteria by 1730 |  |
| 3/25 | CI entrance | Differential <1.0’ | Spillway dive | In criteria at 1730 |  |
| 3/28-29 | CI diffusers | Incorrect position | System in manual | Ops adjusted |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 3/24-26 | WS entrances | Reading <1.5’ | FOG install, F2 work, SDE ROV. | In criteria by 1400 each day. |  |
| 3/26 | Bonneville | No inspection by Fisheries. | Personnel shortage. | Operators did one inspection |  |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 08/09.  It is only out of criteria when tailwater is above 19.0’ msl.

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - Bradford Island temperatures are not available at this time.  The Project is waiting on a new temperature probe.  The new probe should be installed by mid-April.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 3/23 | 39.2 | NA |
| 3/24 | 40.4 | NA |
| 3/25 | 38.5 | NA |
| 3/26 | 37.8 | NA |
| 3/27 | 37.2 | NA |
| 3/28 | 33.2 | NA |
| 3/29 | 34.8 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 29 March.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars began on 21 March.  Stab plates remain installed in gates without exclusion bars.

    - SLEDs (sea lion exclusion devices) and acoustic deterrents are installed at all fishway entrances.

    - WS was set for one fish unit operation from 0220 on 26 March until 1250 on 27 March due to F2 being OOS for servo repairs.

    - SDE was closed from 0909 until 0929 on 28 March to facilitate the ROV inspection of the gate.  Debris was found to be preventing the gate from fully lowering.

  - Juvenile Fishways.

    - U14 orifices were put in manual from 26-28 March to facilitate the gatewell testing that occurred this week.

    - PH1 ITS was closed from 0813 until 1536 on 25 March to facilitate trash raking.

    - The ERG was tripped from 1510 until 1525 on 26 March due to opening too many orifices at once.

    - The B2Cc was closed from 0654 until 1615 on 29 March to facilitate the BGS dive.

  - Lamprey Fishways.  Remain winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - PH2 VBS mods.  All gatewell modifications have been completed.  U16 will return to service on 31 March, U17 returned to service on 26 March.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - BGS.  Re-alignment of the anchors occurred on 29 March.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 20 December replaces the tail water operation for chum spawning teletype on 12 December.  Effective 0600 hours on Monday, December 24, until further notice, operate Bonneville tailwater as follows – minimum 11.5 ft all hours.   The minimum 11.5 ft is for chum incubation.

  - A teletype sent on 25 March requests Bonneville Project to shut off Spill Bay 1, FV5-3, and FV5-4 from 1200-1800 on 25-26 March, and Spill Bay 18, FV4-3, and FV4-4 from 1200-1800 on 27-28 March.  This is necessary to facilitate spillway erosion inspection dives.

  - On 26 March several sturgeon were negatively impacted by the start-up of U17.  Please refer to the MFR sent by Tammy Mackey on 27 March.

  - A teletype sent on 28 March requests Bonneville project to only operate two units plus the fish units at PH2 and close B2CC from 0600 until 1800 on 29 March.  The units operated will be either 11 and 14, or 14 and 18, depending on the location of the dive.  To maintain a minimum tailwater of 11.5’ (see 7.1), the Project can operate PH1 units above the 1%, and if necessary, operate a third PH2 unit at the lower end of 1%.  This operation is necessary to assist with the realignment of the BGS in the PH2 forebay.

JAMES R. MAHAR, P.E.

Operations Manager