### CENWP-OP-B                                                                                                                         April 14, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 15 of 2008, which covers the period from 06 April through 12 April 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 124.9 to 165.2 kcfs.  Daily average project tailwater ranged from 12.1’ to 14.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.6’ to 76.1’ msl.  Daily average river temperature ranged from 45°F to 46°F.  Secchi disk measurements ranged from 5.0 to 6.0.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 1.6 to 99.3 kcfs.  Spill for fish began at 0001 on 10 April.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 9 was out of service from 1216 until 1630 on 11 April for 115kV bus switching.

    - Unit 13 has remained out of service since 27 March for exciter replacement work.

    - Unit 15 has remained out of service since 25 November due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 was out of service from 1230 until 1540 on 10 April due to a problem with the governor.  U16 went out of service at 2130 on 11 April due to the earlier governor problems.

    - Unit 18 was out of service from 0710 until 0748 on 8 April to tighten packing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week:

2.1.1	  FV1-1 was closed for cleaning from 1342 until 1414 on 07 April.

  - STS/VBS Inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  Monitoring with DIDSON acoustic camera and split-beam hydroacoustics near B2CC entrance to estimate the numbers and distribution of kelt-sized targets.  Barge to be removed 16 March.

  - Battelle.  Equipment installation continues in the spillway for a spillway survival evaluation.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling to begin the week of 14 March.

  - Fish Field Unit.  Pinniped observation and scat collection continue.

  - NOAA- Gilbreath.  Juvenile fish releases in gatewell 14A concluded on 6 April.  Next round of testing to occur the week of 14 March.

  - PSMFC Smolt Monitoring. Smolt monitoring activities ongoing.  One steelhead fallback and one chinook fallback were observed crossing the separator bars this week.

  - USDA Wildlife Services. Sea lion hazing from the powerhouses continues.

  - WDFW Fish Counting.  Visual at Bradford Island and WA Shore continues.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 06 April – 12 April.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 4/8, 4/11-12 | A-branch weir | Reading >1.0’ | Unknown | No action taken |  |
| 4/11 | B-Branch | FG3-25 open | System in manual | Ops closed. |  |
| All week | WG 64 | Incorrect position | Brake seized | Waiting on parts to come in. |  |
| CASCADES ISLAND |  |  |  |  |  |
| 4/8 | Cascades Is. | Ent. diff <1.5 | System in manual | Ops adjusted |  |
| 4/11 | Cascades Is. | FG6-12 open | System in manual | Ops closed |  |
| 4/12 | Cascades Is. | FG6-12 off | System in manual | Ops opened |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 4/7-12 | DSM2 | Add-in in manual | Bad channel sensor. | See 4.5.6 and 4.5.7 | 08-37086 |
| 4/7-12 | S. Monolith | Velocity meter reading <1.5’ | Believed to be broken | Cannot replace until winter. |  |
| 4/10-12 | DSM2 | Airburst not bursting all panels | PLC issues. | Electricians working on it. | 08-37503 |

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 09/10.  It is out of criteria when TW is above 19.0’ msl.

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter often reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - Bradford Island temperatures are not available at this time.  The Project is waiting on a new temperature probe.  The new probe should be installed by mid-April.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 4/6 | 38.6 | NA |
| 4/7 | 37.7 | NA |
| 4/8 | 38.9 | NA |
| 4/9 | 39.3 | NA |
| 4/10 | 39.7 | NA |
| 4/11 | 41.7 | NA |
| 4/12 | 45.8 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 11 April.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs and acoustic deterrents remain installed at fishway entrances.

    - U14 orifices were returned to manual at 1206 on 6 April.  Gatewell testing is done until 16 April.

    - DSM2 add-in was placed in manual and reduced to 40cfs from 1412 until 1557 on 7 April due to a bad level sensor reading water elevation as higher than it really is.  If the channel sensor reads the water elevation as too high, it will trip the ERG.  At 1557 the add-in was returned to auto and the channel elevation was controlled by closing F2 orifices.

    - F2 orifices were often moved between auto and manual throughout the week.  Whenever forebay elevation exceeded 75.5’ msl, the orifices would be closed to prevent the channel sensor from tripping the ERG.  Orifices were in auto from:  0201 until 1538 on 8 April; 0550 until 2110 on 9 April; and 0125 on 10 April until 2319 on 11 April.

  - Lamprey Fishways.  Remain winterized.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates will be installed.  Optional items include sloping the floor and removing the DSM wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

  - BGS.  Installation of the acoustic nodes will be completed on 16 March.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - The teletype sent on 20 December, which replaced the tail water operation for chum spawning teletype on 12 December, was replaced by a teletype sent on 11 April.  This teletype, effective immediately, requests 11.5’ minimum tailwater during all hours as a soft constraint.  This request is to protect emerging chum fry.

  - A teletype sent on 10 April requests the project operate in the following manner, with a hard constraint from 0600 on 11 April until 0559 on 15 April 9, a soft constraint from 0600 on 15 April until 0600 on 19 April:

    - Operate PH2 as the priority PH, up to loading criteria in 7.2.2 before operating PH1;

    - Operate PH2 units at the lower end of 1%.  Units will be targeted at about 50MW with a maximum generation of 57MW.

    - Operate PH1 MGR units as first on/last off and within the 1% efficiency range;

    - PH2 units may run to full capacity within 1% to avoid spilling over the gas cap.

    - This operation was requested to facilitate the migration of the four million juvenile tule chinook released by Spring Creek NFH.

  - A teletype sent on 10 April requests the Project to begin juvenile fish spill beginning at 0001 on 10 April and continuing until further notice.  Spill will be 100Kcfs (or as close as the 100K pattern allows given forebay elevation) for 24 hours a day.  The current pattern can be found in the 2008 FPP at www.nwd-wc.usace.army.mil/tmt/documents/fpp/

JAMES R. MAHAR, P.E.

Operations Manager