### CENWP-OP-B                                                                                                                         May 19, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 20 of 2008, which covers the period from 11 May through 17 May 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 239.5 to 298.4 kcfs.  Daily average project tailwater ranged from 19.7’ to 22.3’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 74.7’ msl.  Daily average river temperature ranged from 53°F to 55°F.  Secchi disk measurements ranged from 3.0 to 5.0.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 95.5 to 110.6 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 3 has remained out of service since 14 April for a five year overhaul.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 9 was out of service from 0955 until 1305 on 14 May for hub oil sump drainage.

    - Unit 11 was out of service from 1158 until 2042 on 12 May to facilitate work on the BGS.

    - Unit 12 was out of service from 1204 until 2051 on 12 May to facilitate work on the BGS.  U12 was OOS from 0714 until 1010 on 14 May for governor work.

    - Unit 13 was out of service from 1208 until 2112 on 12 May to facilitate work on the BGS.

    - Unit 15 has remained out of service since 25 November 2007due to exciter and pole failure, followed by a head gate hydraulic line rupture.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

    - On 14 May, operators discovered the VBS sensors were reading low by .1’-.5’, U18 being the worst.  The Project is working to correct this problem.  Until then, the VBSs will be raked starting 19 May and U18 drawdown will be manually measured each day.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week:

    - FV1-1 was closed for cleaning from 1604 until 1634 on 12 May.

    - FV 3-7 was closed for cleaning from 0733 until 0833 on 14 May.

  - STS/VBS Inspections.  STS/VBS inspections scheduled for the week of 19 May.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage. No fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  BGS hydrophone installation was allowed to occur on 12 May.

  - Battelle.  Equipment installation completed for a spillway survival evaluation.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF began 15 April.

  - Fish Field Unit.  Pinniped observation and scat collection continue.

  - NOAA – Gilbreath.  Juvenile Spring Creek fish releases in gatewell 14A continue. PIT tagged fish are being collected in SbyC and SMP samples.

  - NOAA – Jacobson.  Collected 25 chinook and 25 coho from PSMFC for pathogen testing.

  - NOAA – McComas.  Collected 1236 chinook from PSMFC for JSATS and PIT tag testing.

  - NOAA – Pennington.  Lamprey ramps scheduled for water-up on 19 May.  No collection at WS NDE due to TW elevation (platform is at or under water).

  - PSMFC Smolt Monitoring.  14 steelhead and six salmon were recorded crossing the separator bars.  GBT results may be found at http://www.fpc.org/CurrentDaily/Gbtsum.txt.  1261 yearling chinook and 25 coho were held for NOAA researchers and 84 yearling chinook were collected for Univ. of WA.

  - USDA Wildlife Services. Sea lion hazing from the powerhouses continues.

  - University of Washington.  Collection of barged fish, SbyC, and RoR fish for challenge trial continues.   Collected 84 chinook from PSMFC.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 11 – 17 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| All week | FG3-5 | Closed. | Diffuser broken. | See 4.2.4 | 08-38527 |
| 5/14 | A-branch weir | Reading >1.0’ | Unknown | No action- shad mode starts 15 May. |  |
| 5/14, 5/15 | FG3-22 | Incorrect position for TW elev. | System in manual. | Ops adjusted. |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-10 | Incorrect position for TW elev. | Diffuser broken | See 4.2.1 |  |
| 5/13-14 | FG6-9 | Incorrect position for TW elev. | System in manual. | Ops adjusted. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 5/12, 5/14 | Weir 37 & 38 | Reading >1.0’ | Unknown | No action taken. |  |
| 5/16 | Gatewell 18B | VBS diff >1.1’ | Sensor reading incorrectly | U18 on setpoint. | 08-42724 |
| All week | DSM2 airburst | Operating incorrectly | PLC issues. |  | 08-37503 |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have parted ways.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - FV 3-7 in manual due to failure to track FB elevations.  It is adjusted to maintain ladder criteria.  TR 08-39938.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - BI temperatures are not available at this time.   The new probe is installed but not yet programmed.

    - The WS fishway temperature probe is no longer working properly.  Replacement and/or repairs are expected to take a couple of months.  Until then, the AFF probe will be used as a surrogate.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | AFF | BI average |
| --- | --- | --- | --- |
| 5/11 | NA | 51.1 | NA |
| 5/12 | NA | 50.9 | NA |
| 5/13 | NA | 51.3 | NA |
| 5/14 | NA | 52.7 | NA |
| 5/15 | NA | 54.6 | NA |
| 5/16 | NA | 55.6 | NA |
| 5/17 | NA | 56.0 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 17 May.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs and acoustic deterrents remain installed at fishway entrances.

    - WS NDE was closed from 1244 until 1420 on 13 May to facilitate the lamprey ramp deployment.

    - Fishways went to shad passage mode on 15 May.

  - Juvenile Fishways.

    - U14 orifices went to manual on 14 May, A-S open and A-N closed, for NOAA gatewell releases.

    - F1 and F2 orifices were moved to manual throughout the week to maintain DSM2 level.

    - B2CC bulkhead was on seal with the flush valve open from 1212 until 1927 on 12 May to facilitate work on the BGS.

    - Increased descaling rates were observed at the JMF on 14 May.  The Project raked trashracks and found little debris.  Descaling dropped on Thursday.  Increased descaling rates were again seen on 16 May.  The Project was requested to operate PH2 at the lower end of 1% see 7.8.  Descaling did not decrease.  VBSs are scheduled to be cleaned first thing on 19 May.

  - Lamprey Fishways.

    - BI and WS AWS lamprey ramps are scheduled for water-up on 19 May.

    - The WS NDE lamprey ramp was deployed on 13 May.  See 4.5.5

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 April canceled the 11 April teletype requesting minimum tailwater elevations of 11.5’ as a soft constraint.  Chum fry emergence was deemed complete at the 9 April TMT meeting.

  - A teletype sent on 10 April requests the Project to begin juvenile fish spill beginning at 0001 on 10 April and continuing until further notice.  Spill will be 100Kcfs/ 24 hrs a day.  The current pattern can be found in the 2008 FPP at www.nwd-wc.usace.army.mil/tmt/documents/fpp/

  - A teletype sent on 6 May requests U14 be operated as first priority from 0600 on 7 May until 1200 on 12 May to accommodate the NOAA gatewell tests.  A 14 May teletype extended the U14 operation from 1200 on 14 May until 1800 on 18 May.

  - A teletype sent on 12 May authorized BON to flush debris from spillbays 1, 2, 17, and 18 to reduce the risk of damaging research equipment on the main dam piernoses.

  - A teletype sent on 12 May approves an exceedence of the 4’ TW fluctuation limit between 1200 and 1600 on 12 May.  The TW is permitted to fluctuate up to 5’ during those hours while the B2CC is closed for BGS repairs.  The maximum rate of change is 1.5’/hour.

  - A teletype sent on 12 May requests the B2CC be closed and no more than four PH2 units operate from 1200 until 1800 on 12 May to facilitate repairs to the GPS system along the BGS.  In addition, BON may shift flow from PH2 to PH1 and involuntarily spill any excess flow.

  - A teletype sent on 15 May requests a soft constraint for the forebay elevation to be as low as possible from 1100 until 1600 on 17 May.  This is to facilitate a beach clean-up at the kiteboard areas in Lyle, WA.

  - A teletype sent on 16 May requests the Project operate PH2 units between the low end and lower quarter point of 1% (excluding U14) in an effort to reduce descaling rates seen at the JMF.  The Project was authorized to spill above the gas cap as a result of unit operation.

JAMES R. MAHAR, P.E.

Operations Manager