### CENWP-OP-B                                                                                                                         May 26, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 21 of 2008, which covers the period from 18 May through 24 May 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 346.0 to 418.6 kcfs.  Daily average project tailwater ranged from 24.8’ to 29.0’ msl.  Daily average powerhouse forebay elevation ranged from 73.6’ to 74.1’ msl.  Daily average river temperature ranged from 55°F to 56°F.  Secchi disk measurements ranged from 2.5 to 3.0.’

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 152.7 to 230.9 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 3 has remained out of service since 14 April for a five year overhaul.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 was out of service from 0816 until 1028 on 22 May for STS removal.  U11 was at reduced load from 1653 until 1718 on 23 May for trashrack raking.

    - Unit 12 was out of service from 0749 until 0935 on 23 May for STS removal.

    - Unit 13 was out of service from 1043 until 1446 on 23 May for STS removal.

    - Unit 14 was reduced to the lower end of 1%, with orifices in auto at 1200 on 18 May.  U14 was out of service from 0930 until 1352 on 20 May for 14C STS repair.  U14 was out of service from 1503 until 1652 on 23 May for STS removal.

    - Unit 15 has remained out of service since 25 November 2007due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 was out of service from 1104 until 1359 on 22 May for STS removal.

    - Unit 17 was out of service from 1413 until 1616 on 22 May for STS removal.

    - Unit 18 was at reduced load at 2005 on 18 May.  U18 was out of service from 1345 until 1611 on 21 May for STS removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was on standby to float trash from 1057 until 1330 on 21 May.

    - F2 was out of service for trashraking from 1102 until 1332 on 21 May.

  - Gatewell drawdowns are measured on Wednesdays.

    - On 14 May, operators discovered the VBS sensors were reading low by .1’-.5’.  All sensors were calibrated by 21 May.  Additional errors in calibration were found.  The control room continues to check VBS differential manually.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week:

    - FV1-1 was closed for cleaning from 0713 until 0813 on 20 May.  FV1-1 was closed to float trash from 0001 until 0430 on 24 May and from 2200 on 24 May until 0400 on 25 May.

    - FV 3-7 was closed for cleaning from 1247 until 1317 and 1500 until 1548 on 22 May.  FV3-7 was closed to float trash from until 0430 on 24 May and from 2200 on 24 May until 0400 on 25 May.

    - FV3-9 was closed for cleaning from 1247 until 1317 on 22 May.

    - FV5-9 was closed for cleaning from 1249 until 1259 on 22 May.

    - FV6-9 was closed for cleaning from 1308 until 1333 on 22 May and from 1258 until 1306 on 23 May.

  - STS/VBS Inspections.  STS/VBS inspections were scheduled for the week of 18 May.  Instead, STSs were pulled due to high flows and debris loads.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 5/22 |  | STSs pulled. |
| 12 | 5/23 |  | STSs pulled. |
| 13 | 5/23 |  | STSs pulled. |
| 14 | 5/23 |  | STSs pulled. |
| 15 |  |  | Unit OOS. STSs already out. |
| 16 | 5/22 |  | STSs pulled. |
| 17 | 5/22 |  | STSs pulled. |
| 18 | 5/21 |  | STSs pulled. |

  - Dewatering and Fish Salvage. No fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  BGS hydrophones are installed.

  - Battelle.  Equipment installation completed for a spillway survival evaluation.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF began 15 April.

  - Fish Field Unit.  Pinniped observations continue.

  - NOAA – Gilbreath.  Collected 430 chinook from PSMFC for releases in gatewell 14A on 21 May.  There was no release on 23 May due to STS removal. PIT tagged fish are collected in SbyC and SMP samples.

  - NOAA – Jacobson.  Collected 25 coho from PSMFC for pathogen testing.

  - NOAA – McComas.  Collected 528 chinook from PSMFC for JSATS and PIT tag testing.

  - NOAA – Pennington.  Lamprey ramps were placed in service on 19 May.  No collection at WS NDE due to TW elevation (platform is at or under water).  Traps in the AFF are deployed at night.

  - PSMFC Smolt Monitoring.  Seven steelhead and two salmon were recorded crossing the separator bars.  GBT results may be found at http://www.fpc.org/CurrentDaily/Gbtsum.txt.  1318 yearling chinook and 25 coho were held for NOAA researchers, 84 yearling chinook were collected for Univ. of WA.

  - USDA Wildlife Services. Sea lion hazing concluded on May 20th..

  - University of Washington.  Collection of barged fish, SbyC, and RoR fish for challenge trial continues.   Collected 84 chinook from PSMFC.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats stopped in April.

- FISHWAYS

  - Project biologists inspected on 18 – 24 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| All week | FG3-5 | Closed. | Diffuser broken. | See 4.2.4 | 08-38527 |
| 5/21-22 | A-branch weir | Reading >1.3’ | unknown | No action. |  |
| 5/19-24 | B-branch weir | Gauge underwater | High TW | No action. |  |
| 5/21 | B-branch diffusers | Incorrect position for TW elev. | System in manual. | Ops adjusted. |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-10 | Incorrect position for TW elev. | Diffuser broken | See 4.2.1 |  |
| 5/21 | CI diffusers | Incorrect position for TW elev. | System in manual. | Ops adjusted. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 5/20, 23 | PH2 entrances | Differential >2.0’ | Unknown | Ops adjusted |  |
| 5/21-24 | PH2 | STSs pulled | High debris loads |  |  |
| All week | DSM2 airburst | Operating incorrectly | PLC issues. |  | 08-37503 |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have parted ways.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - FV 3-7 in manual due to failure to track FB elevations.  It is adjusted to maintain ladder criteria.  TR 08-39938.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - BI temperatures are not available at this time.   The new probe is installed but not yet programmed.

    - The WS fishway temperature probe is no longer working properly.  Replacement and/or repairs are expected to take a couple of months.  Until then, the AFF probe will be used as a surrogate.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | AFF | BI average |
| --- | --- | --- | --- |
| 5/18 | NA | 56.4 | NA |
| 5/19 | NA | 56.6 | NA |
| 5/20 | NA | 56.9 | NA |
| 5/21 | NA | 56.3 | NA |
| 5/22 | NA | 54.7 | NA |
| 5/23 | NA | 53.7 | NA |
| 5/24 | NA | 54.8 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 24 May.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs and acoustic deterrents remain installed at fishway entrances.

    - Fishways went to shad passage mode on 15 May.

    - FV1-1 and FV3-7 were placed in manual on 23 May due to increased debris, in effort to keep that ladder operational through the weekend.  They were closed at night to float debris off the trashracks.

  - Juvenile Fishways.

    - U14 orifices returned to auto at 1200 on 18 May.  U14 orifices were in manual for NOAA gatewell releases from 21- 23 May.

    - F2 south orifices were closed at 1332 on 20 May to maintain DSM2 elevations.

    - VBSs were cleaned starting 19 May.  On 21 May, a regional decision was made to pull STSs.  STSs were pulled from 21 – 23 May.

  - Lamprey Fishways.

    - BI and WS AWS lamprey ramps were put in service for the season on 19 May.

    - The WS NDE lamprey ramp remained deployed.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 10 April requests the Project to begin juvenile fish spill beginning at 0001 on 10 April and continuing until further notice.  Spill will be 100Kcfs/ 24 hrs a day.  The current pattern can be found in the 2008 FPP at www.nwd-wc.usace.army.mil/tmt/documents/fpp/

  - A teletype sent on 14 May requests U14 be operated as first priority from 1200 on 14 May until 1800 on 18 May to accommodate the NOAA gatewell tests.  A 20 May teletype extended the U14 operation from 1200 on 21 May until 1800 on 25 May.

  - A teletype sent on 16 May requests the Project operate PH2 units between the low end and lower quarter point of 1% (excluding U14) in an effort to reduce descaling rates seen at the JMF.  The Project was authorized to spill above the gas cap as a result of unit operation.  A teletype sent on 18 May cancels this request.

  - A teletype sent on 21 May authorizes the Project remove PH2 STSs and operate the units at the upper end of the 1% efficiency band.  This action is required due to the high flows and debris building up on the VBSs and fishway trashracks.

JAMES R. MAHAR, P.E.

Operations Manager