### CENWP-OP-B                                                                                                                         June 16, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 24 of 2008, which covers the period from 08 June through 14 June 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 342.4 to 403.0 kcfs.  Daily average project tailwater ranged from 25.1’ to 27.7’ msl.  Daily average powerhouse forebay elevation ranged from 72.8’ to 74.1’ msl.  Daily average river temperature ranged from 55°F to 56°F.  Secchi disk measurements ranged from 3.0’ to 4.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 125.5 to 204.0 kcfs.

    - On 27 May, while opening Bay 15 to flush debris, the hoist failed and the gate fell to the sill.  It remains in the closed position leaving a hole in the spill pattern.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 went out of service at 0238 on 12 June due to a loose generator shroud, and remains out of service due to air housing noise.

    - Unit 14 was out of service from 1521 until 1547 on 12 June to rake trash.

    - Unit 13 was out of service from 1624 until 1636 to rake trash.

    - Unit 15 has remained out of service since 25 November 2007due to exciter and pole failure, followed by a head gate hydraulic line rupture.

    - Unit 16 was out of service from 1553 until 1621 on 12 June to rake trash.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

    - On 14 May, operators discovered the VBS sensors were reading low by 0.1’-0.5’.  Additional errors in calibration were found.  The control room continues to check VBS differential manually.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week:

    - FV1-1 was closed down to float debris from 0003 until 0305 on 8 June; and from 2214 on 8 June until 0301 on 9 June.

    - FV3-7 was closed down to float debris from 0003 until 0305 on 8 June; and from 2214 on 8 June until 0301 on 9 June.

      - FV3-7 was placed in manual from 0305 on 8 June until 0710 on 9 June to limit debris accumulation on the trashrack.

      - FV3-7 was closed for cleaning from 0710 until 0735 on 9 June.

    - FV5-9 was closed for cleaning from 0650 until 0709 on 9 June.

    - FV6-9 was closed for cleaning from 0650 until 0709 on 9 June.

  - STS/VBS Inspections.  The following STS/VBS installation/removal occurred this week.  STSs were removed from U11-18 all week due to high debris loads.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | STSs removed. |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this reporting week:

- RESEARCH

  - Battelle.  BGS hydrophones are installed though not functional.  Attempts to repair the hydrophones may occur the week of 15 June.

  - Battelle.  Equipment installation completed for a spillway survival evaluation.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CTUIR.  Received seven lamprey collected by NOAA in the traps at the AFF to date.  Need 23 more for the radio-tagging study and 493 for their translocation project.

  - NOAA – Gilbreath.  No releases occurred this week due to STS removal.

  - NOAA – Jacobson.  No fish collected this week.

  - NOAA – McComas.  69 subyearling Chinook were collected this week.

  - NOAA – Pennington.  Lamprey ramps remain in service.  No collection at WS NDE due to TW elevation (platform is at or under water).  Traps in the AFF are deployed at night.

  - PSMFC Smolt Monitoring.  Five steelhead and four salmon were recorded crossing the separator bars.  GBT results may be found at http://www.fpc.org/CurrentDaily/Gbtsum.txt.  69 subyearling chinook were collected for NOAA--McComas.

  - USDA Wildlife Services. Avian hazing continues.

  - University of Washington.  Research has concluded

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 8-9, 11-14 June.  NOAA inspected on 13 June.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 6/9,13 | PH1 SCC | Entrance diff <1.0’ | Unknown | Ops adjusted |  |
| 6/10 | Bonneville | Inspection not done | Personnel shortage | Operators performed inspection |  |
| All week | FG3-5 | Closed. | Diffuser broken. | See 4.2.4 | 08-38527 |
| All week | A-branch weir | Reading >1.3’ | Unknown | No action. |  |
| All week | B-branch weir | Reading >1.3’ or underwater | High TW | No action. |  |
| 6/9-10,12-14 | B-branch diffusers | Incorrect position | System in manual | Ops adjusted |  |
| All week | Spillbay 15 | Gate on seal | Hoist failure | See 1.2.1 |  |
| CASCADES ISLAND |  |  |  |  |  |
| 6/8,10,12-14 | CI diffusers | Incorrect position | System in manual | Ops adjusted. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| All week | PH2 | STSs pulled | High debris loads |  |  |
| All week | DSM2 airburst | Operating incorrectly | PLC issues. |  | 08-37503 |
| 6/10 | Bonneville | No inspection | Scheduled mtgs. | Operators inspected |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have parted ways, however, so the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have parted ways.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - BI temperatures are not available at this time.   The new probe is installed but not yet programmed.

    - The WS fishway temperature probe is no longer working properly.  Replacement and/or repairs are expected to take a couple of months.  Until then, the AFF probe will be used as a surrogate.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | AFF | BI average |
| --- | --- | --- | --- |
| 6/8 | NA | 51.8 | NA |
| 6/9 | NA | 52.5 | NA |
| 6/10 | NA | 49.1 | NA |
| 6/11 | NA | 48.6 | NA |
| 6/12 | NA | 50.2 | NA |
| 6/13 | NA | 52.8 | NA |
| 6/14 | NA | 52.7 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 14 June.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs were removed from PH2 entrances on 10 June and from B-branch on 11 June.  They remain installed at Cascades Island and PH1 fishway entrances.

    - Fishways remain in shad passage mode.

    - BI exit was closed for cleaning on 9 June.

  - Juvenile Fishways.

    - On 21 May, a regional decision was made to pull STSs.  STSs were pulled from 21 – 23 May.  Unit 11 STSs were installed on 28 May to monitor debris accumulation on the VBSs.  Due to high VBS drawdowns after roughly 24 hours, U11 STSs were removed.  U11 STSs were re-installed on 2 June and, due to high drawdowns, were removed on 5 June.

  - Lamprey Fishways.

    - WS AWS lamprey ramps remain in service.

    - BI AWS lamprey ramp was taken out of service on 13 June due to pumps supplying insufficient water.  The ramp will be returned to service as soon as possible.

    - The WS NDE lamprey ramp remains deployed, the platform remains under water.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 10 April requests the Project to begin juvenile fish spill beginning at 0001 on 10 April and continuing until further notice.  Spill will be 100Kcfs/ 24 hrs a day.  The current pattern can be found in the 2008 FPP at www.nwd-wc.usace.army.mil/tmt/documents/fpp/

  - A teletype sent on 21 May authorizes the Project remove PH2 STSs and operate the units at the upper end of the 1% efficiency band.  This action is required due to the high flows and debris building up on the VBSs and fishway trashracks.

  - A teletype sent on 9 June requests the project re-install Powerhouse 2 STSs in Units 11 and 14, and operate Units 11 and 14 and all other Powerhouse 2 units according to 2008 FPP.

  - A teletype sent on 9 June cancels the teletype sent on 060908 (see 7.3) due to high flows.

  - A teletype sent on 10 June requests the Project to maintain forebay between 71.5’-73.0’ msl, soft constraint, from 0800-1700 hours on Saturday, June 15.  This is necessary for Port of Hood River beach clean up.

JAMES R. MAHAR, P.E.

Operations Manager