### CENWP-OP-B                                                                                                                         June 30, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 26 of 2008, which covers the period from 22 June through 28 June 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 300.9 to 372.5 kcfs.  Daily average project tailwater ranged from 22.8’ to 25.9’ msl.  Daily average powerhouse forebay elevation ranged from 73.2’ to 75.2’ msl.  Daily average river temperature ranged from 60°F to 62°F.  Secchi disk measurements ranged from 3.5’ to 5.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 87.7 to 155.0 kcfs.

    - On 27 May, while opening Bay 15 to flush debris, the hoist failed and the gate fell to the sill.  It remains in the closed position.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 5 was out of service from 1311 until 1331 on 27 June due to a line trip.

    - Unit 6 was out of service from 1311 until 1331 on 27 June due to a line trip.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 has remained out of service since 0238 on 12 June due to rotor cracks.

    - Unit 14 was out of service from 0825 until 1035 on 22 June due to turbine bearing oil cooler.

    - Unit 18 was placed on setpoint control with reduced load at 1342 until 1620 on 27 June to reduce VBS drawdown, until screens were cleaned.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

    - On 14 May, operators discovered the VBS sensors were reading low by 0.1’-0.5’.  Additional errors in calibration were found.  The sensors have sense been calibrated and are functioning, but are still monitored manually.

- ACTIVITIES

  - AWS Closures.  No AWS closures occurred this reporting week.

  - STS/VBS Inspections.  No STS/VBS video inspections occurred this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  BGS hydrophones are installed and are now functional.  Reinstallation occurred 23-25 June and involved 2 tugs and a safety boat.  Corner collector bulkhead was held by a crane in the slot in case an emergency closure was necessary.  Closure was unnecessary and the operation was successful with no incidents.

  - Battelle.  Spillway survival evaluation continues.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CTUIR.  Received sixty nine lamprey collected by NOAA at the AFF to date for restoring lamprey to the Umatilla River.

  - NOAA – Gilbreath.  No gatewell releases occurred this week due to STS removal.  Releases are scheduled to resume the week of 30 June.

  - NOAA – Jacobson.  Collected 12 subyearling chinook from PSMFC for pathogen testing.

  - NOAA – McComas. Collected 546 subyearling chinook from PSMFC for JSATS and PIT tag testing.

  - NOAA – Moser.  Trapping and PIT tagging at the AFF continues.  The WA shore north downstream entrance is in operation as of 24 June.

  - PSMFC Smolt Monitoring.  Condition, index, and gas bubble trauma monitoring at the SMF.  Please contact deanb@gorge.net for results.  Five salmon and four steelhead were recorded crossing the separator bars.  558 subyearling chinook were collected for researchers.

  - University of Idaho.  Combining daytime, estimated nighttime, LPS counts and detections from radio and HD PIT sites to determine the best methods to estimate system wide passage of adult Pacific lamprey.  Working in the experimental flume at the AFF on lamprey passage improvements.

  - USDA Wildlife Services. Avian hazing continues.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 22-28 June.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| All week | A-branch diffuser | FG 3-5 Incorrect position. | Diffuser broken. | See 4.2.4 | 08-38527 |
| 6/22, 23 | A-branch staff gage | Water elevation >1.3 | Unknown |  |  |
| 6/26-27 | B-branch diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 6/23, 24, 26 | B-branch entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| SPILLWAY |  |  |  |  |  |
| All week | Spillbay 15 | Gate on seal | Hoist failure | See 1.2.1 |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG 6-10 | Incorrect position | Diffuser broken | See 4.2.1 |  |
| 6/26-27 | CI diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 6/23 | CI entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 6/28 | Weir 37 staff gage | Water elevation >1.3 | Shad on bleed off valve | Ops cleaned valve |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated and the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - BI temperatures are not available at this time.   The new probe is installed but not yet programmed.

    - The WS fishway temperature probe has an upgraded power source as of 18 June.

    - The AFF temperature probe power source is being upgraded.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 6/22 | 60.6 | NA |
| 6/23 | 60.9 | NA |
| 6/24 | 61.0 | NA |
| 6/25 | 61.2 | NA |
| 6/26 | 61.4 | NA |
| 6/27 | 62.1 | NA |
| 6/28 | 62.8 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 28 June.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Installation of the FOG sea lion exclusion bars has halted due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs were removed from PH2 entrances on 10 June, from B-branch on 11 June, and from PH1 entrances on June 17.  They remain installed at Cascades Island fishway entrances and will be removed the week of Jun 30th when the new crane arrives.

    - Fishways remain in shad passage mode.

  - Juvenile Fishways.

  - Lamprey Fishways.

    - WS and BI AWS lamprey ramps remain in service.

    - The WS NDE lamprey ramp returned to service.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 17 June authorizes the Project to dog open Spillbay 14 at 2 stops (approx. 2.9’) beginning at 0700 on 18 June.  Spill shall be maintained as specified in the 041008 teletype (see 7.1).  This operation is necessary to repair the Spillbay 15 hoist.  Spillbay 14 will return to normal service once repairs are complete.

  - A teletype sent on 20 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 10 April.

    - From 0001 on 21 June until 2400 on 20 July, Bonneville will spill 85K during daytime hours and to the gas cap at night.

    - From 0001 on 21 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours and to the 120% gas cap at night.

    - The spill pattern is found in section 2, Table BON-15 of the 2008 FPP, and daytime hours are defined in section 2, Table BON-5 of the 2008 FPP.  www.nwd-wc.usace.army.mil/tmt/documents/fpp/

    - At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”.

    - At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

  - A teletype sent on 23 June authorizes the Project to dog open Spillbays 11, 14, and 18 at 2 stops (approx. 2.9’) beginning as soon as possible.  Spill shall be maintained as specified in the 061908 teletype (see 7.2).  This operation is necessary to repair the Spillbay 15 hoist.  Spillbays 11, 14, and 18 will return to normal service once repairs are complete.

  - A teletype sent on 27 June requests the Project to maintain forebay between 75.0’-76.5’ msl, hard constraint, from 1200 on Thursday, July 03 until 2400 hours on Friday, July 04.  This is needed to prevent access to the Hood River fireworks staging area.

  - A teletype sent on 27 June requests the Project operate Bonneville Pool with soft constraint of 1.0’ operating range, and a hard constraint operating range of 1.5’ from 0600 on Thursday 01 July until 1800 hours on 03 July.  This operation is requested for treaty gillnet fishing.  These dates are a revision of a previous teletype, same subject, sent on 27 June.

JAMES R. MAHAR, P.E.

Operations Manager