### CENWP-OP-B                                                                                                                         July 7, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 27 of 2008, which covers the period from 29 June through 05 July 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 289.4 to 330.9 kcfs.  Daily average project tailwater ranged from 22.2’ to 24.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.6’ to 76.0’ msl.  Daily average river temperature ranged from 63°F to 65°F.  Secchi disk measurements ranged from 4.0’ to 5.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 84.5 to 118.9 kcfs.

    - Bay 15 remains on seal.  On 27 May, while opening Bay 15 to flush debris, the hoist failed and the gate fell to the sill.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 3 was out of service from 0732 until 0752 on 01 July for PT bus inspection.

    - Unit 4 was out of service from 0755 until 0816 on 01 July for PT bus inspection.

    - Unit 5 was out of service from 1505 until 1530 on 02 July due to a line trip.

    - Unit 6 was out of service from 1505 until 1532 on 02 July due to a line trip.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 9 was out of service from 0356 on 01 July until 1730 on 02 July for pre-rehab testing.

    - Unit 10 was out of service from 1431 until 1522 on 30 June for bank 7/8 low side testing.

    - Unit 11 has remained out of service since 0238 on 12 June due to rotor cracks.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

    - VBS sensors have been calibrated and are functioning.  Manual monitoring continues.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week.

    - FV 3-7 was closed for cleaning from 0742 until 0807 on 30 June.

    - FV 3-9 was closed for cleaning from 0807 until 0843 on 30 June.

  - STS/VBS Inspections.  No STS/VBS video inspections occurred this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  BGS hydrophones are installed and are now functional.

  - Battelle.  Spillway survival evaluation continues.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CTUIR.  Received 103 lamprey to date collected by NOAA at the Adult Fish Facility (AFF) for restoring lamprey to the Umatilla River.

  - NOAA – Gilbreath.  Collected 872 chinook from PSMFC for releases in gatewell 14A the week of 30 June.  PIT tagged fish are collected in SbyC and SMP samples.

  - NOAA – Jacobson.  Collected 25 subyearling chinook from PSMFC for pathogen testing.

  - NOAA – McComas. Collected 565 subyearling chinook from PSMFC for JSATS and PIT tag testing.

  - NOAA – Moser.  Trapping and PIT tagging at the AFF continues.  The WA shore north downstream entrance is in operation as of 24 June.

  - PSMFC Smolt Monitoring.  Collection and monitoring continue.  One salmon was recorded crossing the separator bars.  1462 subyearling chinook were collected for researchers.

  - University of Idaho.  Combining daytime, estimated nighttime, LPS counts and detections from radio and HD PIT sites to determine the best methods to estimate system wide passage of adult Pacific lamprey.  Working in the experimental flume at the AFF on lamprey passage improvements.

  - USDA Wildlife Services. Avian hazing continues.

  - USGS.  Collected 35 adult American shad from the AFF.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 29 June-5 July.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| All week | A-branch diffuser | FG 3-5 Incorrect position. | Diffuser broken. | See 4.2.4 | 08-38527 |
| 7/1 | A-branch staff gage | Water elevation >1.3 | Unknown |  |  |
| 6/29 | B-branch diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 7/1,4 | B-branch entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| 7/3 | PH1 entrances | Differential >2.0 | WG1 jammed | Ops adjusted |  |
| SPILLWAY |  |  |  |  |  |
| All week | Spillbay 15 | Gate on seal | Hoist failure | See 1.2.1 |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG 6-10 | Incorrect position | Diffuser broken | See 4.2.1 |  |
| 6/29, 7/3 | CI diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 6/29, 7/2-4 | CI entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| WASHINGTON SHORE |  |  |  |  |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated and the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - BI temperatures are available as of 05 July.

    - The WS fishway temperature probe has an upgraded power source as of 18 June.

    - The AFF temperature probe power source is being upgraded.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | BI average |
| --- | --- | --- |
| 6/29 | 63.7 | NA |
| 6/30 | 64.0 | NA |
| 7/1 | 64.1 | NA |
| 7/2 | 64.1 | NA |
| 7/3 | 64.5 | NA |
| 7/4 | 64.8 | NA |
| 7/5 | 64.9 | 63.7 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 05 July.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Removal of the FOG sea lion exclusion bars has not yet begun due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - SLEDs were removed from Cascades Island fishway entrances the week of 30 June.

    - Fishways remain in shad passage mode.

  - Juvenile Fishways.

  - Lamprey Fishways.

    - WS and BI AWS lamprey ramps remain in service.

    - The WS NDE lamprey ramp remains in service.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 19 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 10 April.

    - From 0001 on 21 June until 2400 on 20 July, Bonneville will spill 85K during daytime hours and to the gas cap at night.

    - From 0001 on 21 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours and to the 120% gas cap at night.

    - The spill pattern is found in section 2, Table BON-15 of the 2008 FPP, and daytime hours are defined in section 2, Table BON-5 of the 2008 FPP.  www.nwd-wc.usace.army.mil/tmt/documents/fpp/

    - At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”.

    - At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

  - A teletype sent on 23 June authorizes the Project to dog open Spillbays 11, 14, and 18 at 2 stops (approx. 2.9’).  Spill shall be maintained as specified in 7.1.  This is to facilitate repairs to the Spillbay 15 hoist.

  - A teletype sent on 27 June requests the Project to maintain forebay between 75.0’-76.5’ msl, hard constraint, from 1200 on 3 July until 2400 on 4 July.  This is to restrict access to the Hood River fireworks staging area.

  - A teletype sent on 27 June requests the Project operate Bonneville Pool with soft constraint of 1.0’ operating range, and a hard constraint operating range of 1.5’ from 0600 on 1 July until 1800 hours on 3 July.  This operation is requested for treaty gillnet fishing.   A teletype on 3 July updates this teletype by extending the operation from 0600 on 8 July until 1800 on 10 July.

  - A teletype sent on 1 July requests U14 be operated as first priority from 1200 on 1 July until 1200 on 5 July to accommodate the NOAA gatewell tests.

JAMES R. MAHAR, P.E.

Operations Manager