### CENWP-OP-B                                                                                                                         July 21, 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 28 of 2008, which covers the period from 13 July through 19 July 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 160.4 to 220.9 kcfs.  Daily average project tailwater ranged from 14.1’ to 17.9 msl.  Daily average powerhouse forebay elevation ranged from 73.8’ to 76.0’ msl.  Daily average river temperature ranged from 67°F to 69°F.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are included in the spill pattern.  Daily average spill ranged from 85.7 to 91.7 kcfs.

    - Bay 15 remains on seal.  On 27 May, while opening Bay 15 to flush debris, the hoist failed and the gate fell to the sill.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 1 went out of service at 0804 on 07 July for five year overhaul.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 12 September 2006 for turbine rehab.

    - Unit 11 has remained out of service since 0238 on 12 June due to rotor cracks.

    - Unit 13 was out of service from 2204 on 13 July until 1613 on 16 July for annual maintenance.

    - Unit 14 was out of service from 1512 until 1608 on 19 July to adjust packing.  Unit 14 was operated at the middle range of 1% at 1200 on 15 July until 1154 on 17 July to facilitate gatewell testing.  U14 operated at the upper 1% range from 1154 on 17 July until at 1200 on 19 July when gatewell testing concluded.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

    - VBS sensors have been calibrated and are functioning.  Manual monitoring continues.

- ACTIVITIES

  - AWS Closures.  The following AWS closures occurred this reporting week.

    - FV 3-7 was closed for cleaning from 0720 until 1040 on 16 July.

    - FV 3-9 was closed for cleaning from 0720 until 1040 on 16 July.

    - FV 6-9 was closed for cleaning from 1549 until 1613 on 15 July.

  - STS/VBS Inspections.  No STS/VBS video inspections occurred this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage. The following fish salvage activities occurred this reporting week:

    - Fish were salvaged from Unit 8 tail logs on 14 July.  Four juvenile chinook, one juvenile steelhead, two sturgeon, four sculpins, and one bass were recovered.  All were released in good condition.

- RESEARCH

  - Battelle.  BGS hydrophones are installed and are now functional.

  - Battelle.  Spillway survival evaluation continues.

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CTUIR.  Received 142 lamprey to date collected by NOAA at the Adult Fish Facility (AFF) for restoring lamprey to the Umatilla River.

  - NOAA – Gilbreath.  Collected 842 chinook from PSMFC for releases in gatewell 14A the week of 13 July.  PIT tagged fish are collected in SbyC and SMP samples.

  - NOAA – Jacobson.  Collected 25 subyearling chinook from PSMFC for pathogen testing.

  - NOAA – McComas. Collected 554 subyearling chinook from PSMFC for JSATS and PIT tag testing.

  - NOAA – Moser.  Trapping and PIT tagging at the AFF continues.

  - PSMFC Smolt Monitoring.   Condition, index, and gas bubble trauma monitoring at the SMF.  Please contact deanb@gorge.net for results.  Three adult steelhead were recorded crossing the separator bars.  1421 subyearling chinook were collected for NOAA.

  - University of Idaho.  Combining daytime, estimated nighttime, LPS counts and detections from radio and HD PIT sites to determine the best methods to estimate system wide passage of adult Pacific lamprey.  Working in the experimental flume at the AFF on lamprey passage improvements.

  - USDA Wildlife Services. Avian hazing continues.

  - USGS.  No shad collections this week.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 13-19 July.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 7/13 | A-branch diffuser | FG 3-5 Incorrect position. | Diffuser broken. | See 4.2.4 | 08-38527 |
| 7/14,19 | B-branch diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 7/19 | B-branch entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| SPILLWAY |  |  |  |  |  |
| All week | Spillbay 15 | Gate on seal | Hoist failure | See 1.2.1 |  |
| CASCADES ISLAND |  |  |  |  |  |
| 7/19 | CI diffusers | Incorrect position | System in manual | Ops adjusted |  |
| 7/19 | CI entrance | Differential > 2.0 | System in manual | Ops adjusted |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 7/17 | 14B VBS | Not seated properly | Gantry failure | VBS lowered ASAP |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated and the diffuser will not be operational until repaired in winter 09/10.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It’s OOC at TW 16.7’ msl and higher.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will not be made until winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

    - Bradford Island temperatures are not available at this time.

Table 3.  Bonneville Fishway Temperatures

| Date | WS average | AFF | SMF |
| --- | --- | --- | --- |
| 7/13 | 67.2 | 67.2 | 66.2 |
| 7/14 | 67.8 | 67.8 | 66.9 |
| 7/15 | 68.2 | 68.4 | 67.4 |
| 7/16 | 68.2 | 68.3 | 67.5 |
| 7/17 | 67.9 | 68.0 | 67.2 |
| 7/18 | 67.7 | 67.7 | 66.9 |
| 7/19 | 67.5 | 67.5 | 66.6 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 18 July.

    - B-Branch and Cascades Island fishway PLC are in manual.

    - Removal of the FOG sea lion exclusion bars has not yet begun due to a broken lifting beam.  The four large orifices have bars (two at each end of the powerhouse). The stab plates remain installed in gates without exclusion bars.

    - Fishways remain in shad passage mode.

    - Cascades Island exit is open as of 0840 on 11 July, to provide an exit for sockeye trapped upstream of the UMT picket leads.

  - Juvenile Fishways.

    - U14-A orifices were in manual for NOAA gatewell releases from 15 – 19 July.

    - U14-B VBS was not seated properly from 1030 until 1121 on 17 July due to gantry crane failure.

  - Lamprey Fishways.

    - WS and BI AWS lamprey ramps remain in service.

    - The WS NDE lamprey ramp remains in service.

- CONSTRUCTION

  - PH1 ITS Wall Removal.  Three automated gates to be installed.  May slope the floor and remove the wall.

  - TIE crane.  The TIE crane boom repair is on hold until funding is secured.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 19 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 10 April.

    - From 0001 on 21 June until 2400 on 20 July, Bonneville will spill 85K during daytime hours and to the gas cap at night.

    - From 0001 on 21 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours and to the 120% gas cap at night.

    - The spill pattern is found in section 2, Table BON-15 of the 2008 FPP, and daytime hours are defined in section 2, Table BON-5 of the 2008 FPP.  www.nwd-wc.usace.army.mil/tmt/documents/fpp/

    - At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”.

    - At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

  - A teletype sent on 23 June authorizes the Project to dog open Spillbays 11, 14, and 18 at 2 stops (approx. 2.9’).  Spill shall be maintained as specified in 7.1.  This is to facilitate repairs to the Spillbay 15 hoist.

  - A teletype sent on 14 July requests U14 be operated as first priority from 1200 on 15 July until 1200 on 19 July to accommodate the NOAA gatewell tests.

  - A teletype sent on 16 July requests the Project operate Bonneville Pool with soft constraint of 1.0’ operating range, and a hard constraint operating range of 1.5’ from 0600 on 22 July until 1800 hours on 24 July.  This operation is requested for treaty gillnet fishing.

  - A teletype sent on 17 July authorizes the Project to deviate from unit priority, as stated in the Table 11 of the 2008 FPP, and operate the Unit 8 outside the 1% range as necessary, beginning 18 July to approximately 31 July.  It is requested that operation outside of the 1% be kept to a minimum.  This is necessary to facilitate startup and commissioning testing for Unit 8 with the new minimum gap runner.

  - A teletype sent on 17 July requests the Project to maintain Bonneville forebay elevation about 75.0 msl from 0900 to 1500 on 19 July, soft constraint.  This operation is requested for 0900 to 1500 on 20 July, if possible.  This operation is requested for Gorge Games Outrigger race.

  - Warm Springs collected 20 lamprey for ceremonial purposes from the AFF on 18 July.

JAMES R. MAHAR, P.E.

Operations Manager