### CENWP-OP-B                                                                                                                                      05 October 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40of 2008, which covers the period from 28 September through 04 October 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 74.1 to 107.0 kcfs.  Daily average project tailwater ranged from 7.7’ to 9.9’ msl.  Daily average powerhouse forebay elevation ranged from 75.9’ to 76.2’ msl.  Daily average river temperature stayed at 65°F.  Secchi disk measurements averaged 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.3 to 1.5 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 4 was out of service from 0355 until 1941 on 30 September to facilitate substation work.  U4 was out of service from 0958 until 1211 on 2 October to facilitate the Gantry 4 load test.

    - Unit 5 was out of service from 0655 until 1910 on 30 September to facilitate substation work.

    - Unit 6 was out of service from 0655 until 1910 on 30 September to facilitate substation work.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 was out of service from 0655 until 1910 on 30 September to facilitate substation work.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor cracks.

    - Unit 12 was out of service from 0808 until 1622 on 1 October due to transmission line load limits.

    - Unit 13 moved up in unit priority from 0743 until 1358 on 29 September to facilitate moving fish away from Unit 11 prior to tail log placement.  U13 was out of service from 0655 until 1946 on 30 September to facilitate substation work.  U13 was out of service from 0803 until 1628 on 1 October due to transmission line load limits.

    - Unit 14 was out of service from 1631 until 1926 on 30 September and from 0801 until 1633 on 1 October due to transmission line load limits.

    - Unit 15 has remained out of service since 05 September due to rotor pole failure.

    - Unit 16, which has been out of service since 03 September due to transmission line load limits, returned to service at 1624 on 1 October.

    - Unit 17 was out of service from 0805 until 1623 on 1 October due to transmission line load limits.

    - Unit 18 was out of service from 0815 until 1618 on 1 October due to transmission line load limits.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 0210 until 2118 on 1 October to facilitate switchyard work.

    - F2 was out of service from 0210 until 2118 on 1 October to facilitate switchyard work.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV1-1 was closed for cleaning from 1500 until 1515 on 2 October.

    - FV3-7 was closed for cleaning from 1022 until 1100 on 2 October.

    - FV3-9 was closed for cleaning from 1049 until 1110 on 29 September.

  - STS/VBS inspections.

No STS/VBS video inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | N/A | N/A | N/A |

  - Dewatering and Fish Salvage.  The following fish salvage activity occurred this reporting week.

    - Unit 11 draft tube was dewatered on 30 September.  Biologists removed 35 sturgeon, six channel catfish, three bullheads and one northern pikeminnow.  All were released alive and well.

- RESEARCH

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - NOAA – Gilbreath.  Saltwater tag effects study continues.

  - NWW fish trucking.  Releases occur every other day.

  - PSMFC Smolt Monitoring.  Condition, index, and GBT monitoring continue.  One chinook adult and one chinook jack were recorded crossing the separator bars.  No research fish collected.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.  Tule counting concluded on 30 September.

- FISHWAYS

  - Project biologists inspected on 28 September through 4 October.  NOAA Fisheries inspected on 3 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |
| 9/28-10/4 | A-branch weir | Reading >1.0’ | Unknown | No action taken |  |
| 9/29, 10/1-2 | B-branch entrance | Differential <1.0> | System in manual | Ops adjusted. |  |
| 9/29, 10/3 | PH1 PCC | Differential <1.0 | Sensors broken | Ops adjusted. |  |
| CASCADES ISLAND |  |  |  |  |  |
| 9/29, 10/1 | CI entrance | Differential <1.0> | System in manual | Ops adjusted |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 9/29 | South diffusers | Incorrect positions | Manual operation | Ops adjusted. |  |
| 10/1 | Fish units | OOS | Transmission line work. | Back in service at 2118. |  |
| 10/1 | North and south monoliths | No head or velocity | Fish units OOS | Back in service at 2118. |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will be made in winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT channel and the main ladder at Washington shore.  Temperatures are in ºF.

Table 3.  Bonneville Fishway Temperatures

| Date | WA shore | Bradford Is. |
| --- | --- | --- |
| 9/28 | 65.2 | NA |
| 9/29 | 65.0 | NA |
| 9/30 | 65.1 | NA |
| 10/1 | 65.5 | NA |
| 10/2 | 65.7 | NA |
| 10/3 | 65.8 | NA |
| 10/4 | 65.5 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 2 October.

    - B-Branch and Cascades Island fishway PLCs are in manual.

    - Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.

    - Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.

    - STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.

    - On 30 September, the Bradford Is. fishway exit was closed for cleaning from 1630 until 1650.

  - Juvenile Fishways.

  - Lamprey Fishways.

    - BI and WA shore AWS lamprey ramps remain in service.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway (ITS) Wall Removal.  Three automated gates to be installed.

  - TIE crane.  The TIE crane boom repair contract is currently out for bid.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletypes sent on 26 September authorizes a deviation from Bonneville unit priority, as listed in table BON-11 of the 2008 Fish Passage Plan, beginning at 0001 on 29 September until tail log installation is completed.  During this time, the PH2 unit priority will be 11, 18, 12, 13, 15, 17, 14, 16.  This is necessary to guide fish away from Unit 11, prior to unit dewatering.

  - A teletype sent on 26 September requests the Bonneville forebay be maintained between 75’-76.5’ as a hard constraint and between 75.5’ and 76.5’ as a soft constraint from 0600 on 29 September until 1800 hours on 3 October.  This operation is requested to limit wear and tear on gill net equipment, facilitate work on The Dalles spill wall, and to provide a steady pool for White Salmon River fish salvage.

  - A teletype sent on 3 October, and in place until further notice, requests the Bonneville forebay be maintained between 75.0’-76.5’ msl as a hard constraint and between 75.5’ and 76.5’ msl as a soft constraint.  This operation is requested to facilitate the TDA spillway work and the White Salmon river fish salvage.

JAMES R. MAHAR, P.E.

Operations Manager