### CENWP-OP-B                                                                                                                                      19 October 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 42of 2008, which covers the period from 12 through 18 October 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 79.6 to 131.3 kcfs.  Daily average project tailwater ranged from 7.5’ to 11.8’ msl.  Daily average powerhouse forebay elevation ranged from 76.0’ to 76.4’ msl.  Daily average river temperature ranged from 60ºF to 61ºF.  Secchi disk measurements ranged from 4.5’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.2 to 1.3 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 2 was out of service from 0842 until 1158 on 9 October due to a loose wicket gate shear pin.

    - Unit 3 was out of service from 2059 on 13 October until 1311 on 15 October for annual maintenance.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 was out of service from 0624 until 0808 on 16 October for annual maintenance.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor cracks.

    - Unit 15 has remained out of service since 05 September due to rotor pole failure.

    - Unit 17 went out of service at 2113 on 13 October for annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Fish unit trashracks were raked at 1545 on 15 October.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS video inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | N/A | N/A | N/A |

  - Dewatering and Fish Salvage.  No fish salvage activity occurred this reporting week.

- RESEARCH

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - NOAA – Gilbreath.  Saltwater tag effects study continues.

  - NWW fish trucking.  Releases occur every other day.

  - PSMFC Smolt Monitoring.  Condition, index, and GBT monitoring continue.  One steelhead adult was recorded crossing the separator bars.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 12 through 18 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |
| 10/12-13, 10/17 | A-branch weir | Reading >1.0’ | Unknown | No action taken |  |
| 10/15 | PH1 entrances | Head diff <1.0’ | FV1-1 in manual | FV1-1 in Auto |  |
| 10/15-16 | B-branch ent. | Differential <1.0’ | System in manual | Ops adjusted. |  |
| 10/15-16, 10/18 | B-branch diffusers | Incorrect position | System in manual | Ops adjusted. |  |
| CASCADES ISLAND |  |  |  |  |  |
| 10/15 | CI entrance | Differential <1.0’ | System in manual | Ops adjusted |  |
| 10/15, 10/18 | CI diffusers | Incorrect position | System in manual | Ops adjusted |  |
| WASHINGTON SHORE – no out of criteria items |  |  |  |  |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will be made in winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT channel and the main ladder at Washington shore.  Temperatures are in ºF.

Table 3.  Bonneville Fishway Temperatures

| Date | WA shore | Bradford Is. |
| --- | --- | --- |
| 10/12 | 61.4 | NA |
| 10/13 | 60.8 | NA |
| 10/14 | 60.6 | NA |
| 10/15 | 60.8 | NA |
| 10/16 | 60.8 | NA |
| 10/17 | 60.7 | NA |
| 10/18 | 60.8 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 17 October.

    - B-Branch and Cascades Island fishway PLCs are in manual.

    - Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.

    - Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.

    - STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.

  - Juvenile Fishways.

  - Lamprey Fishways.  BI and WA shore AWS lamprey ramps remain in service.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Three automated gates to be installed.

  - TIE crane.  The TIE crane boom repair contract is currently out for bid.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 3 October, in place until further notice, requests the Bonneville forebay be maintained between 75.0’-76.5’ msl as a hard constraint and between 75.5’ and 76.5’ msl as a soft constraint.  This operation is requested to facilitate TDA spillway work and White Salmon river fish salvage.

  - A teletype sent on 17 October requests restricted operation of PH2 units 12-18 from 0600 until 1800, each day, during 20-22 October.  This action is requested to reduce velocities in the PH2 forebay during the BGS inspection dives.  Fish units and PH1 are to be operated per 2008 FPP criteria.

JAMES R. MAHAR, P.E.

Operations Manager