### CENWP-OP-B                                                                                                                                      27 October 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2008, which covers the period from 19 through 25 October 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 87.4 to 125.2 kcfs.  Daily average project tailwater ranged from 8.3’ to 10.9’ msl.  Daily average powerhouse forebay elevation ranged from 75.9’ to 76.4’ msl.  Daily average river temperature ranged from 58ºF to 60ºF.  Secchi disk measurements ranged from 6.5’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.2 to 1.3 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 0 was out of service from 0300 on 20 October until 1258 on 23 October for governor wiring modifications.

    - Unit 1 was out of service from 0059 on 21 October until 1623 on 23 October leak repairs to the governor oil pressure tank.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor cracks.

    - Unit 13 was out of service from 0431 until 1627 on 20 October, 0436 until 1321 on 21 October, and 0503 until 1615 on 22 October for the Behavioral Guidance System (BGS) dive inspection.

    - Unit 14 was out of service from 0431 until 1627 on 20 October, 0436 until 1321 on 21 October, and 0503 until 1636 on 22 October for the BGS dive inspection.  Was out of service from 0647 until 1105 on 23 October for Submersible Traveling Screen (STS) repairs.

    - Unit 15 has remained out of service since 05 September due to rotor pole failure.

    - Unit 16 was out of service from 0431 until 1618 on 20 October, 0436 until 1329 on 21 October, and 0503 until 1628 on 22 October for the BGS dive inspection.

    - Unit 17 went out of service at 2113 on 13 October until 1658 on 21 October for annual maintenance.  Was out of service from 0503 until 1630 on 22 October for the BGS dive inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week:

2.1.1	FV 3-9 was closed for cleaning from 1122 until 1200 on 20 October.

2.1.2	FV 6-9 was closed for cleaning from 1108 until 1119 on 20 October.

  - STS/VBS inspections.  The following STS/VBS video inspections occurred this week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1 | 10/27 | 674 | OK |
| 3 | 10/27 | 540 | OK |
| 11 | 10/23 | 0 | Out of Service |
| 12 | 10/23 | 840 | OK |
| 13 | 10/23 | 494 | OK |
| 14 | 10/23 | 806 | 14A - repaired splices and put back in service |
| 15 | 10/23 | 0 | Out of service |
| 16 | 10/23 | 359 | OK |
| 17 | 10/23 | 636 | OK |
| 18 | 10/23 | 776 | OK |

  - Dewatering and Fish Salvage.  No fish salvage activity occurred this reporting week.

- RESEARCH

  - CRITFC.  Annual chinook, coho, sockeye and steelhead sampling in the AFF concluded on 14 October.

  - NOAA – Gilbreath.  Saltwater tag effects study continues.

  - NWW fish trucking.  Releases occur every other day.

  - PSMFC Smolt Monitoring.  Condition, index, and GBT monitoring continue.  One adult and one jack chinook were recorded crossing the separator bars.  Smolt monitoring operations will conclude for the season at 0700 on 31 October.

  - WDFW Fish Counting.  Visual counts at Bradford Island and WA Shore continue.

- FISHWAYS

  - Project biologists inspected on 19 through 25 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion |  | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |  | ##### TR# |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |  |  |
| 10/19-22 | B-branch diffusers | Incorrect position |  | System in manual |  | Ops adjusted. |  |
| 10/22 | A-branch weir | Reading <1.0’ |  | FV3-9 not controlling properly |  | Ops adjusted. |  |
| 10/22 | B-branch weir | Reading <1.0’ |  | FV3-9 not controlling properly |  | Ops adjusted. |  |
| 10/22 | BI weir | Reading <1.0’ |  | FV3-9 not controlling properly |  | Ops adjusted. |  |
| 10/11 | PH1 S. entrance | Head diff <1.0’ |  | FV1-1 in manual |  | Ops adjusted. |  |
| 10/23, 25 | B-branch entr. | Differential <1.0’> |  | System in manual |  | Ops adjusted. |  |
| 10/23 | B-branch entr. gates | Incorrect position |  | System in manual |  | Ops adjusted |  |
| CASCADES ISLAND |  |  |  |  |  |  |  |
| 10/23 | CI entrance | Differential <1.0’ |  | System in manual |  | Ops adjusted |  |
| 10/23, 25 | CI entr. gates | Incorrect position |  | System in manual |  | Ops adjusted |  |
| 10/19-23 | CI diffusers | Incorrect position |  | System in manual |  | Ops adjusted |  |
| WASHINGTON SHORE – no out of criteria items |  |  |  |  |  |  |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.

    - PH1 elec. velocity meter is in an eddy.  Readings for FPP criteria are taken at the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - FG3-5 closed.  The shaft and gate have separated.  Repairs scheduled for winter 09/10.  It is OOC when TW is above 16.7’ msl.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Repairs will be made in winter 08/09.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT channel and the main ladder at Washington shore.  Temperatures are in ºF.

Table 3.  Bonneville Fishway Temperatures

| Date | WA shore | Bradford Is. |
| --- | --- | --- |
| 10/19 | 60.6 | NA |
| 10/20 | 60.2 | NA |
| 10/21 | 59.7 | NA |
| 10/22 | 59.1 | NA |
| 10/23 | 58.5 | NA |
| 10/24 | 58.4 | NA |
| 10/25 | 58.0 | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 25 October.

    - B-Branch and Cascades Island fishway PLCs are in manual.

    - Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.

    - Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.

    - STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.

  - Juvenile Fishways.

  - Lamprey Fishways.  BI and WA shore AWS lamprey ramps remain in service.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Three automated gates to be installed.

  - TIE crane.  The TIE crane boom repair contract has been awarded.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 3 October, in place until further notice, requests the Bonneville forebay be maintained between 75.0’-76.5’ msl as a hard constraint and between 75.5’ and 76.5’ msl as a soft constraint.  This operation is requested to facilitate TDA spillway work and White Salmon river fish salvage.

  - A teletype sent on 17 October requests restricted operation of PH2 units 12-18 from 0600 until 1800, each day, during 20-22 October.  This action is requested to reduce velocities in the PH2 forebay during the BGS inspection dives.  Fish units and PH1 are to be operated per 2008 FPP criteria.

JAMES R. MAHAR, P.E.

Operations Manager