### CENWP-OD-B                                                                                                                                  22 December 2008

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 51 of 2008, which covers the period from 14 through 20 December 2008.

- OPERATION SUMMARY

  - Daily average river flows ranged from 124.8 to 162.6 kcfs.  Daily average project tailwater ranged from 12.2’ to 13.6’ msl.  Daily average powerhouse forebay elevation ranged from 74.0 to 75.1’ msl.  Daily average river temperature ranged from 43ºF to 46ºF.  Secchi disk measurements ranged from 4.0’ to 7.0’.

  - Spill Bay 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill was 0.5 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor cracks.

    - Unit 12 was out of service from 1133 until 1444 on 16 December for STS removal.

    - Unit 13 was out of service from 0637 until 0852 on 16 December for STS removal.

    - Unit 14 was out of service from 0858 until 1127 on 16 December for STS removal.

    - Unit 15 returned to service at 1137 on 17 December. It had been out of service since 05 September due to rotor pole failure.

    - Unit 16 was out of service from 0629 until 0859 and from 1036 until 1352 on 17 December for STS removal.

    - Unit 17 was out of service from 1338 until 1559 on 15 December for STS removal.

    - Unit 18 was out of service from 1041 until 1325 on 15 December for STS removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Unit F1 has remained out of service since 01 December for annual maintenance.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1, 3-7, and 3-9 remain closed for winter maintenance in A-branch.

    - FV 4-3 and 4-4 remain closed for winter maintenance in B-branch.

    - FV6-9 was closed for cleaning from 1508 until 1522 on 18 December.

  - STS/VBS inspections.  No  STS/VBS video inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 3 | NA | NA | Scheduled for removal for ITS modifications in late January |
| 11-18 | NA | NA | Scheduled for removal the week of 15 December. |

  - Dewatering and Fish Salvage.  The following fish salvage or dewatering activities occurred this week:

    - On 18 December DSM2 was dewatered.  No fish were salvaged, but a cormorant was rescued and returned to the wild.

- RESEARCH

  - WDFW Fish Counting.  Daily video counting at Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 16-18 December.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND – OOS for winter maintenance |  |  |  |  |  |
| CASCADES ISLAND – nothing to report |  |  |  |  |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 12/17, 12/18 | PH2 entrances | Differential <1.0’ | Excessive debris on F2 trashrack | Riggers cleaned |  |
| 12/17 | FV 6-9 | Trashrack drawdown | Excessive debris | Riggers cleaned |  |
| All week | SA-24 board | Not reading | OOS for repairs |  |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.

    - PH2 velocity meter.  The velocity meter is believed to be broken.  Plans are to replace with a mechanical meter.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 18 December.

    - Cascades Island fishway PLC is in manual.

    - Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.

    - Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.

    - STSs were installed on 15 September in Units 1 and 3 for adult fallback.  DSM1 is running south.

    - FV6-9 was put in manual at 0343 on 04 December.  The valve was not properly controlling in auto.

    - Bradford Island fishway has been out of service since 3 December for winter maintenance.  Flow remains out of FG3-18 to move sturgeon and to prevent a need to unnecessarily handle large numbers of sturgeon.

    - The Adult Fish Facility went to orifice flow at 1442 on 01 December.  It was scheduled to be dewatered on 22 December but activities were cancelled due to bad weather.

  - Juvenile Fishways.

    - The JMF remains in bypass.

    - DSM1 dewatering has been scheduled for late January.

    - DSM2 was dewatered on 18 December. See 2.3.1.

  - Lamprey Fishways.  BI and WA shore AWS lamprey ramps are winterized.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.

  - TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.

- HAZMAT, SPILLS AND CLEANUP

  - At 2012 on 16 December, the gearbox on the STS in Unit 18C was found to be leaking oil.  The STS had been removed from the water on 15 December and exceptionally cold weather caused the gearbox seal to fail.  All oil was contained in the 18C gatewell slot.  The orifice was closed and oil absorbents were deployed. No oil was released into the river.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 November establishes the upper BON forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.

  - A teletype sent on 12 November requests BON tailwater operations for chum spawning.  It requests a tailwater elevation hard constraint of a minimum of 11.3’ msl during all hours and between 11.3’ to 11.7’ msl between 0600 and 1800 hours daily.  Target elevation is 11.5’ msl.

  - Winter maintenance began on 1 December.  For a complete list of dewatering activities, please contact Project Fisheries.

  - A teletype sent on 16 December replaces the teletype sent on 12 November regarding BON tailwater operations for chum spawning.  It requests a tailwater elevation hard constraint of a minimum of 11.3’ msl during all hours and between 11.3’ to 11.7’ msl between 0600 and 1500 hours daily.  Target elevation is 11.5’ msl.

JAMES R. MAHAR, P.E.

Operations Manager