### CENWP-OD-B                                                                                                                                  04 January 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 1 of 2009, which covers the period from 28 December 2008 through 03 January 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 120.3 to 178.5 kcfs.  Daily average project tailwater ranged from 12.5’ to 17.8’ msl.  Daily average powerhouse forebay elevation ranged from 74.8’ to 75.8’ msl.  Daily average river temperature ranged from 38ºF to 39ºF.  Secchi disk measurements were between 2.0’ and 7.0’.

  - Spill Bay 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.6 kcfs.

  - Unit Operation.  Powerhouse 2 is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 17 December due to turbine bearing failure.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor cracks.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 has remained out of service since 01 December for annual maintenance.

    - F2 was on standby from 1115 until 1430 on 31 December to facilitate U17 and U18 trashrack raking.  F2 is schedule to go out of service on 10 January.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1, FV3-7, FV3-9, FV4-3 and FV4-4 remain closed for winter maintenance.

    - Weir 37 was closed from 1825 until 2334 on 28 December to float trash.

  - STS/VBS inspections.  No STS/VBS video inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 3 | NA | NA | Scheduled for removal for ITS modifications in late January |
| 11-18 | NA | NA | Removed for season. |

  - Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.

- RESEARCH

  - WDFW Fish Counting.  Daily video counting at Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 29-31 December, and 02-03 January.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND – OOS for winter maintenance |  |  |  |  |  |
| CASCADES ISLAND |  |  |  |  |  |
| 12/29, 1/2 | CI entrance | Head <1.0’ | System in manual | Operators corrected. |  |
| 12/29, 1/2-3 | CI diffusers | incorrect position | System in manual | Operators opened. |  |
| 1/2-3 | CI diffusers | FG6-12 closed | No power | Operators TR’d |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 1/2-3 | WS monoliths | <1.0’ differential | SUE/SDE fully open | Please see 4.5.7 |  |
| 1/2-3 | N. monolith | NUE/NDE closed | SUE/SDE fully open | Please see 4.5.7 |  |
| DSM1/ITS |  |  |  |  |  |
| All week | ITS chain gate | 7A closed | Unknown | Structural crew notified. Gates to be adjusted 1/5 |  |
| DSM2/ JMF – OOS for winter maintenance |  |  |  |  |  |

    - FG6-10 closed.  The motor was repaired on 15 August 2007.  The shaft and gate have separated.  The diffuser will not be operational until repaired in winter 08/09.  It is OOC when TW is above 19.0’ msl.

    - PH2 velocity meter.  The velocity meter is broken.  It will be replaced with a mechanical meter.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 30 December.

    - DSM1 is running south.  STSs remain installed Units 1 and 3 for adult fallback.  Dewatering is scheduled for late January.

    - BI fishway remains OOS for winter maintenance.  FG3-18 continues to provide flow to B-branch.

    - Cascades Island fishway PLC is in manual.

    - Cascades Island exit remains open to provide an exit for fish upstream of the UMT picket leads.

    - Due to a broken lifting beam, sea lion exclusion bars remain installed in the four large FOGs.  Stab plates remain installed in the smaller FOGs.

    - Since 23 October 2008, the south monolith entrances (SUE and SDE) have been without control power and have remained in the fully open position.  On 2 January 2009, tailwater raised to about 17’.  With only one fish unit available, entrance differential could not be maintained above 1.0’.  In an attempt to increase entrance differential to >1.0’, NUE was closed and NDE set to a 6’ opening.  On 3 January, operators manually raised SUE to a 13’ opening (FPP criteria).  This raised the entrance differential to 1.1’.

    - FV6-9 returned to auto at 1358 on 31 December.

    - The AFF remains at orifice flow.  Dewatering is scheduled to occur on 5 January.

  - Juvenile Fishways.

    - DSM2 remains dewatered.  The two-mile pipe is scheduled to be inspected on 15 January.

  - Lamprey Fishways.  BI and WS AWS lamprey ramps are winterized.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.

  - TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 November establishes the upper BON forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.

  - A teletype sent on 22 December requests a minimum Bonneville forebay elevation of 73.4’ msl through 28 December, soft constraint.  This operation was requested by the Port of Cascade Locks in an effort to prevent damage due to ice in the Cascade Locks Marina.

  - A teletype sent on 16 December, regarding BON tailwater operations for chum spawning, was replaced by a teletype sent on 30 December.  The new teletype requests a hard constraint for a minimum tailwater elevation of 11.3’ msl during all hours and between 11.3’ and 13.0’ msl during all hours.  If necessary, the project is authorized to raise tailwater up to 18.5’ msl between 1500-0600 hours.

  - A teletype sent on 31 December, regarding BON tailwater operations for chum egg incubation, replaced the 30 December teletype (see 7.3).  It requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice.

  - Winter maintenance continues.  For a complete list of dewatering activities, please contact Project Fisheries.

JAMES R. MAHAR, P.E.

Operations Manager