### CENWP-OD-B                                                                                                                                  26 January 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 4 of 2009, which covers the period from 18 through 24 January 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 164.1 to 193.1 kcfs.  Daily average project tailwater ranged from 14.3’ to 16.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.9’ msl.  Daily average river temperature ranged from 39ºF to 40ºF.  Secchi disk measurements were between 2.0’ to 4.0’.

  - Spill Bay 18, which provides attraction flow for B-Branch, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to .7 kcfs.

    - Spill Bay 2 was opened 1’ from 1512 until 1700 on 23 January to provide flushing flow during sturgeon salvage efforts in the CI entrance.  The flow was used to keep sea lions from crowding the release site.

  - Unit Operation.  Powerhouse 1 remains the priority powerhouse.

    - Unit 1 was out of service from 1117 until 1407 on 21 January for trashrack raking.

    - Unit 2 was out of service from 0740 until 1124 on 22 January for trashrack raking.

    - Unit 3 was out of service from 1128 until 1555 on 22 January for trashrack raking.

    - Unit 4 was out of service from 0718 until 1110 on 23 January for trashrack raking.

    - Unit 5 was out of service from 1113 until 1525 on 23 January for trashrack raking.

    - Unit 6 was out of service from 1528 until 1629 on 23 January and from 1204 until 1337 on 24 January for trashrack raking.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 10 was out of service from 1525 until 1622 on 24 January for trashrack raking.

    - Unit 11 has remained out of service since 12 June due to rotor damage.

    - Unit 12 returned to service at 1700 on 20 January after being out since 14 January.  Sea lion observers reported seeing 10-15 sturgeon floating downstream at 1700 on 20 January, following the U12 start-up.  U12 was started using the new, slow roll procedures.

    - Unit 14 was out of service from 1411 until 1556 on 21 January for trashrack raking.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 and F2 remain out of service while the WS fishway is dewatered.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1 was closed from 1325 until 1400 on 21 January for cleaning.

    - FV3-7 was closed from 0743 until 0810 on 20 January for cleaning.

    - FV5-3, FV5-4, FV5-9 and FV6-9 remain closed while Cascades Island and WS remain dewatered.

  - STS/VBS inspections.  No STS/VBS activities occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 3 | 1/7 | NA | Removed until 15 September. |
| 11-18 | NA | NA | Six STSs have broken gearboxes due to freezing in December. |

  - Dewatering and Fish Salvage.  The following fish salvage and dewatering activities occurred this week:

    - On 20 January Fisheries, along with volunteers from CRITFC and WDFW, salvaged fish from Cascades Island.  From the CI exit and AWS they removed five clipped juvenile steelhead, one unclipped juvenile steelhead, one juvenile chinook, three sculpin, approximately 100 stickleback, one bass, one sucker, one whitefish, one peamouth, three crayfish.  One dead unclipped juvenile steelhead was recovered.

    - On 20 January Fisheries, along with volunteers from WDFW, CRITFC and PSMFC, removed one clipped adult steelhead, three juvenile steelhead, two sculpin and five stickleback from the UMT.

    - On 22 January Fisheries removed eight adult steelhead from diffuser pools FG6-5 through FG6-10.

    - On 23 and 24 January Fisheries, along with volunteers from Project Maintenance and PSMFC, removed 400-500 sturgeon and six peamouth from the CI entrance.  They recovered one dead clipped adult steelhead that died due to the dewatering.  They recovered one dead sturgeon that died due to getting trapped under a man basket during the recovery effort.  A memo was sent on 24 January regarding the dead steelhead and the large numbers of stranded sturgeon.  Please contact Project Fisheries for a copy.

- RESEARCH

  - WDFW Fish Counting.  Video counting at Cascades Island concluded on 20 January.  Video counting at Bradford Island continues.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats began on 06 January.

- FISHWAYS

  - Project biologists inspected 18, 21-22 January.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |
| 1/22 | B-branch entr. | Head <1.0’ | System in manual | Operators adjusted. |  |
| CASCADES ISLAND- OOS for winter maintenance |  |  |  |  |  |
| WASHINGTON SHORE- OOS for winter maintenance |  |  |  |  |  |
| DSM1/ITS – DSM1 is OOS until early September |  |  |  |  |  |
| DSM2/ JMF – OOS for winter maintenance |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 22 January.  B-branch PLC remains in manual.

    - WG 2 remains in manual due to an inability to raise >10.9’.

    - Cascades Island was dewatered on 20 January.

    - WS fishway remains dewatered.

    - The AFF remains dewatered.

    - SLEDS remain in stalled at B-Branch.

  - Juvenile Fishways.

    - DSM1 remains dewatered.

    - DSM2 remains dewatered.

  - Lamprey Fishways.  BI and WS AWS lamprey ramps are winterized.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Automated gate installation in FY09.  Wall removal in FY10.

  - TIE crane.  The TIE crane boom repair contract has been awarded.  Completion expected in Spring ‘09.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.

  - A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice.

  - A 23 January teletype requests spillbay 2 be opened one stop from 1500 until 1700 on 23 January.  This is to provide flushing flow during the sturgeon salvage efforts in the Cascades Island entrance.

JAMES R. MAHAR, P.E.

Operations Manager