### CENWP-OD-B                                                                                                                                  01 March 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 9 of 2009, which covers the period from 22 through 28 February 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 114.2 to 156.5 kcfs.  Daily average project tailwater ranged from 11.6’ to 14.4’ msl.  Daily average powerhouse forebay elevation ranged from 74.1’ to 76.0’ msl.  Daily average river temperature was 38ºF.  Secchi disk measurements ranged from 5.0’ to 6.4’.

  - Spill Bay 18, which provides attraction flow for B-Branch, is open 6” during daylight hours.  Daily average spill ranged from 0.6 to 0.7 kcfs.

  - Unit Operation.  Powerhouse 1 remains the priority powerhouse until 1 March.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor damage.

    - Unit 12 was out of service from 1331 until 1458 on 23 February for trashrack raking and from 1115 until 1329 on 26 February for STS installation.

    - Unit 13 was out of service from 1502 until 1554 on 23 February for trashrack raking and from 0921 until 1110 on 26 February for STS installation.

    - Unit 14 was out of service from 1140 until 1326 on 23 February for trashrack raking and from 0645 until 0921 on 26 February for STS installation.

    - Unit 15 was out of service from 1052 until 1136 on 23 February for trashrack raking; from 0652 until 1036 on 24 February for trashrack repair and from 1419 until 1608 on 25 February for STS installation.

    - Unit 16 was out of service from 1021 until 1048 on 23 February for trashrack raking and from 1137 until 1419 on 25 February for STS installation.

    - Unit 17 was out of service from 0848 until 1021 on 23 February for trashrack raking and from 0930 until 1136 on 25 February for STS installation.

    - Unit 18 was out of service from 0710 until 0842 on 23 February for trashrack raking and from 0707 until 0925 on 25 February for STS installation.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 returned to service at 1338 on 28 February.

    - F2 remains out of service for packing.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV5-3 and FV5-4 returned to service at 1500 on 28 February.

    - FV5-9 returned to service at 1109 on 28 February.

    - FV6-9 returned to service at 1040 on 28 February.

  - STS/VBS inspections.  The following STS/VBS activities occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 3 | NA | NA | Removed until 15 September. |
| 11 | NA | NA | U11 remains OOS |
| 12-14 | 2/26 |  | STSs installed. |
| 15-18 | 2/25 |  | STSs installed. |

  - Dewatering and Fish Salvage.  The following fish salvage and dewatering activities occurred this week:

    - On 25 February Fisheries removed 48 sturgeon from the PH2 C-5 diffuser pit.

- RESEARCH

  - WDFW Fish Counting.  Video counting at Bradford Island continues.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected 24, 26-28 February.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |
| 2/26-27 | A-branch weir | Reading <1.0’> | Unknown | No action taken. |  |
| 2/26-27 | B-branch diffusers | FG3-26 incorrect position for TW | System in manual. | Operators adjusted. |  |
| 2/27-28 | B-branch diffusers | FG3-25 incorrect position for TW | System in manual. | Operators adjusted. |  |
| 2/28 | B-Branch | Low differential | System in manual | Operators adjusted |  |
| CASCADES ISLAND- returned to service on 28 February |  |  |  |  |  |
| WASHINGTON SHORE- returned to service on 28 February |  |  |  |  |  |
| 2/28 | Weir 37 | Staff gauge gone | Moved for AFF picket leads. | Riggers to re-install next week. |  |
| DSM1/ITS – DSM1 is OOS until early September |  |  |  |  |  |
| 2/28 | ITS | Not in service | Contractors delayed | Will be watered up on 3/2 |  |
| DSM2/ JMF – returned to service on 24 February |  |  |  |  |  |
| 2/28 | 11A-N, 11C-S | Closed | 11A-N has air leak. 11C-N jammed. | TR’d | 09-119557 |
| 2/28 | 13A-N | Orifice light off | Bad light fixture | TR’ | 09-119562 |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 27 February.  B-branch PLC remains in manual.

    - WG 2 remains in manual due to an inability to raise >10.9’.

    - Cascades Island returned to service at 1500 on 28 February.  All SLEDs were installed by 1534 on 27 February.

    - WS fishway returned to service at 1040 on 28 February.

    - The AFF remains dewatered.

  - Juvenile Fishways.

    - DSM1 remains dewatered.

    - DSM2 returned to service at 1400 on 24 February.  Hydrocannons were turned on at 1108 on 26 February.

    - PH1 ITS remains dewatered for automated gate installation.

  - Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Gate installation continues.  Wall removal in FY10.

  - TIE crane.  The TIE crane boom repair has been delayed.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A 06 November teletype set the BON upper forebay limit as 76.5’ msl. and the lower limit as 71.5’ msl.

  - A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 1 January 2009 until further notice.

  - A 26 February teletype requests Unit 6 be placed as last on/first off in the unit priority list.  This is to accommodate the alignment measurement and testing of Unit 7.  Unit 6 will return to normal FPP unit priority when the Unit 7 work has been completed or at 0001 on 13 March, whichever comes first.

JAMES R. MAHAR, P.E.

Operations Manager