### CENWP-OD-B                                                                                                                                  23 March 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 12 of 2009, which covers the period from 15 through 21 March 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 115.8 to 150.4 kcfs.  Daily average project tailwater ranged from 11.6’ to 13.7’ msl.  Daily average powerhouse forebay elevation ranged from 75.4’ to 76.0’ msl.  Daily average river temperature ranged from 40 - 42ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-Branch, respectively, are open 6” during daylight hours.  Daily average spill was 1.3 kcfs on each day during the reporting period.

  - Unit Operation.  Powerhouse 2 was the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 has remained out of service since 17 December due to generator lower guide bearing failure.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor damage.

    - Unit 15 was out of service from 0001 on 18 March until 0019 on 19 March.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valve was closed this reporting week:

    - FV1-1 was closed for cleaning from 1609 until 1624 on 19 March.

  - STS/VBS inspections.  No STS/VBS activities occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 2 | NA | NA | Removed until 3 September. |
| 11 | NA | NA | U11 remains OOS |
| 12-18 | NA |  | STSs installed. |

  - Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.

- RESEARCH

  - CRITFC- JMF video.  The viewing window has been installed in the sample flume at the Juvenile Monitoring Facility (JMF).

  - NOAA- spill gate test.  Vibration sensors scheduled for installation on Spillbay 11 on 29 March.

  - NOAA- B2CC PIT.  Fish releases scheduled for 15 April.

  - NOAA-FGE.  Fish releases scheduled for 25 March.

  - PNNL- BGS.  Trailers will be delivered the week of 23 March.

  - PSMFC- Smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallback counter installed at separator.

  - WDFW Fish Counting.  Video counting at Bradford Island began on 10 January and at Washington Shore on 01 March.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats and trapping continues.

  - USDA Wildlife Services. Hazing from shore continues.

- FISHWAYS

  - Project biologists inspected 15-21 March.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |  |
| 3/20-21 | A-branch weir | Reading >1.0’ | Unknown | No action taken. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| Nothing to report |  |  |  |  |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| 3/18 | PH2 collection channel | South diffuser gates closed | In manual due to calibrations | Operators corrected |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - Fisheries is working with maintenance to build and install a mechanical velocity meeting at the PH2 south monolith.  For now, there is no velocity meter.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 3/15 | 39.5 | 39.2 |
| 3/16 | 39.6 | 39.4 |
| 3/17 | 39.9 | 39.6 |
| 3/18 | 40.2 | 39.9 |
| 3/19 | 40.6 | 40.3 |
| 3/20 | 40.9 | 40.6 |
| 3/21 | 41.2 | 40.9 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 20 March.

    - B-branch PLC remains in manual.  New transducers have been installed.  Fisheries will monitor accuracy before returning to auto.  Cascades Island PLC is not functioning at all.  Repairs are expected to be made the week of 23 March.

    - 11 FOGs are in service, one remains out of service until structural repairs can be made.

    - The AFF remains dewatered.

    - Weir 37 staff gauge was installed on 16 March.

  - Juvenile Fishways.

    - The PH1 ice and trash sluiceway is in service.   Automated gates are installed in slots 3B, 6C, and 10B and set to elevation 71 feet.  Chaingates 1B and 1C are also open and set to elevations 71’ and 73’ respectively. Wiring and programming is not yet complete.

    - The Smolt Monitoring Facility was switched to bypass from 0700 until 1500 on 19 March for repairs.

  - Lamprey Fishways.  BI and WS AWS lamprey ramps remain winterized.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal is scheduled for FY10.

  - TIE crane.  The TIE crane boom repair has been delayed.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A 06 November teletype set the BON upper forebay limit as 76.5’ msl and the lower limit as 71.5’ msl.

  - A 31 December teletype, regarding BON tailwater operations for chum egg incubation, requests a minimum tailwater elevation of 11.5’ msl during all hours from 0001 on 01 January 2009 until further notice.

  - A 26 February teletype requests that Unit 6 be placed as last on/first off in the unit priority list.  This is to accommodate the alignment measurement and testing of Unit 7.  Unit 6 will return to normal FPP unit priority when the Unit 7 work has been completed or at 0001 on 13 March, whichever comes first.

JAMES R. MAHAR, P.E.

Operations Manager