### CENWP-OD-B                                                                                                                                  03 May 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 18 of 2009, which covers the period from 26 April through 02 May 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 226.8 to 298.1 kcfs.  Daily average project tailwater ranged from 18.3’ to 22.7’ msl.  Daily average powerhouse forebay elevation ranged from 73.7’ to 74.9’ msl.  Daily average river temperature ranged from 50ºF to 51ºF.  Secchi disk measurements ranged from 3.0’ to 4.5’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-Branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 94.6 to 101.4 kcfs.

    - Bay 17 remains set at two dogs.

    - Bay 1 was closed from 2200 until 2256 on 01 May to facilitate the installation of the new Cascades Island entrance weir.

  - Unit Operation.  Powerhouse 2 remains the priority powerhouse.

    - Unit 0 was out of service from 0642 until 1229 on 30 April due to Bank 1/2 maintenance.

    - Unit 4 was out of service from 0942 until 1139 on 29 April to facilitate a brush replacement.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August for turbine rehab.

    - Unit 11 has remained out of service since 12 June due to rotor damage.

    - Unit 12 was out of service from 1414 until 1518 on 27 April due to a transformer trip signal from the North Bonneville sub-station.

    - Unit 13 was out of service from 1414 until 1518 on 27 April due to a transformer trip signal from the North Bonneville sub-station.

    - Unit 14 was out of service from 1414 until 1520 on 27 April due to a transformer trip signal from the North Bonneville sub-station.  U14 was out of service from 0639 until 1720 on 28 April for the preferred AC panel replacement.

    - Unit 15 was out of service from 1414 until 1518 on 27 April due to a transformer trip signal from the North Bonneville sub-station.  U15 was out of service from 0622 until 1656 on 30 April for the preferred AC panel replacement.

    - Unit 16 was out of service from 1414 until 1515 on 27 April due to a transformer trip signal from the North Bonneville sub-station.  U16 was out of service from 0837 until 1709 on 29 April for the preferred AC panel replacement.

    - Unit 17 was out of service from 1414 until 1537 on 27 April due to a transformer trip signal from the North Bonneville sub-station.

    - Unit 18 was out of service from 0810 until 1918 on 27 April for the preferred AC panel replacement.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 1414 until 1526 on 27 April due to a transformer trip signal from the North Bonneville sub-station.

    - F2 was out of service from 1414 until 1719 on 27 April due to a transformer trip signal from the North Bonneville sub-station.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week.

    - FV3-7 was closed for cleaning from 1520 until 1535 on 29 April.

    - FV3-9 was closed for cleaning from 1520 until 1535 on 29 April.

    - FV5-3/FV5-4 was closed from 2220 until 2259 on 01 May to facilitate the installation of the new Cascades Island entrance weir.

    - FV6-9 was closed for cleaning from 0750 until 0757 on 28 April.

  - STS/VBS inspections.  The following STS/VBS activities occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1-2 | NA | NA | Remain out of service until 3 September. |
| 11-18 | NA | NA | No inspections this reporting week. |

  - Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.

- RESEARCH

  - CRITFC- JMF video.  Video equipment for monitoring juvenile fish passage at the JMF scheduled for installation the week of 10 May.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - FFU- sea lion.  Sea lion observations continue.

  - NOAA- spill gate test.  Vibration sensors remain installed on Spill bay 6.

  - NOAA-FGE.  Test releases of PIT-tagged Spring Creek NFH fish continued this week to assess passage conditions at two turbine operating ranges (middle and low-middle of the 1% efficiency range).  Test fish were released at the intake into unit 14A.

  - NOAA Lamprey.  Cascades Island lamprey ramp installation concluded this week.  Water-up for all lamprey passage structures scheduled for the week of 18 May.

  - NOAA – Determination of pathogen prevalence in juvenile salmonids.  Collected 25 yearling chinook and 15 coho from the JMF.

  - PNNL- BGS.  All hydrophones are installed and collecting data for the BGS evaluation.

  - PSMFC- Smolt monitoring.  Daily condition and index monitoring continues.  Fallbacks recorded crossing the separator bars included; 22 steelhead , 14 salmon, and one unknown salmonid.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  84 yearling chinook were collected for University of Washington and 25 yearling chinook and 15 coho were held for NOAA this week.

  - WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways.

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats and trapping continues.

  - University of Idaho.  Tagging adult spring chinook at the AFF to monitor passage at the restructured Cascades Is. entrance weir.  The new entrance weir is designed to improve adult lamprey passage.

  - University of Washington.  Barge versus bypass fish testing for latent mortality continues.  Collected 84 yearling chinook from the JMF.

  - USDA Wildlife Services. Hazing sea lions from shore continues.  Avian hazing began on 01 April.

- FISHWAYS

  - Project biologists inspected 26 April through 02 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND |  |  |  |  |  |  |
| 4/26-27 | B-Branch FG3-23 | Stuck mid-way | Broken motor. | Repaired on 4/27. | 09-143465 |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |  |
| 4/28 | Entrance diff. | Reading >2.0’ | Imbalance between FV5-3 and FV5-4. | Ops adjusted. |  |  |
| 4/29 | CI fishway | Construction within 50’ | No prior coordination | Please see 4.5.3 |  |  |
| 5/01 | CI entrance | No differential. | FV5-3/5-4 closed for weir install | Back in criteria at 2259 |  |  |
| 5/01 | Bay 1 | Closed | CI entrance weir install | Back in criteria at 2256 |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| All week | WS temp probe | Not recording | Unknown | Sending in for repair. |  |  |
| All week | NUE | No staff gauge | Gauge stops at 17’ | Estimated water level |  |  |
| 4/27 | Entrance diff | Reading <1.0’ | Fish units off | Please see 7.3 |  |  |
| 4/30 | WS monoliths | Entrances too high | System in manual | Ops lowered entrances |  |  |
| ITS – nothing to report |  |  |  |  |  |  |
| DSM2/ JMF |  |  |  |  |  |  |
| 4/27 | DSM2 | ERG tripped | PH2 offline | Please see 7.3 |  |  |
| 4/27 | DSM2 | Orifices closed | PH2 offline | Please see 7.3 |  |  |
| 4/27 | Upper switchgate | In bypass | PH2 offline | Please see 7.3 |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

    - CI south entrance gate remains broken and closed.  It is out of criteria when TW is <17’.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

    - The Washington Shore temperature probe has not been recording temperatures.  The cause of this is unknown.  The unit will need to be sent in for repairs.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 4/26 | NA | 49.0 |
| 4/27 | NA | 49.0 |
| 4/28 | NA | 49.1 |
| 4/29 | NA | 49.3 |
| 4/30 | NA | 49.4 |
| 5/01 | NA | 49.4 |
| 5/02 | NA | 49.6 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 02 May.

    - B-branch and Cascades Island PLC’s remain in auto.

    - On 23 April, NOAA Fisheries began phase two of the CI lamprey ramp installation, installing the flume above diffusers FG6-16 through 6-20, along the walkway between the fishway and Spillbay 1.  This involved using a rotohammer to install approximately 24 anchors ( 1/2” diameter 5 ½” long wedge anchors) as well as working in close proximity to the fishway.  It takes about 30 seconds to drill each hole.  Much of the work was located above the dead zone in front of the old fish elevators.  Project Fisheries modified the work schedule on 29 April so installation could be completed.

    - The new Cascades Island entrance weir was installed at 2200 on 01 May.

    - The Washington Shore fishway entrances are in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening.

    - On 27 April, the Washington Shore fishway entrances were out of criteria due to PH2 tripping offline.  Please see 7.3 for more information.

  - Juvenile Fishways.

    - Spillbay 17 remains on two dogs.  The bay should be at 3.5’ but due to a broken hoist it has to be dogged instead.  Flow is compensated through adjacent bays.

    - On 27 April, the DSM2 ERG tripped open and the JMF upper switchgate moved to bypass due to PH2 tripping offline.  Please see 7.3 for more information.

    - Spillbay 1 was closed from 2200 until 2256 on 01 May to facilitate the CI entrance weir installation.

  - Lamprey Fishways.

    - The CI entrance weir was installed between 2200 and 2250 on 01 May.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal is scheduled for FY10.  Old DSM bypass equipment in the tailrace is scheduled for removal in FY10 as well.

    - The electrical work for the automated gates is currently scheduled to be complete on 13 May, with testing on 15 May.

  - TIE crane.  The new boom is to arrive at BON in Mid June and load testing should happen by the first week in July.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 09 April requests spring spill to begin at 0001 on 10 April, continuing until further notice.

  - A teletype sent on 24 April requested a tailwater soft constraint tailwater elevation not to exceed 24.5’ msl from 0830 on 28 April until 0830 on 29 April.  The official Project tailwater elevation gauge is located at river mile 144.5.  This request is to facilitate a release from the Tanner Creek fish hatchery.

  - Due to a transformer trip signal from the BPA North Bonneville Substation, PH2 units tripped offline at about 1400 on 27 April.  All ten units were out of service, however units 11 and 18 were already out of service for scheduled repairs.  With no turbine capacity at PH2, the Control Room followed FPP spill patterns, except for Bay 17 which remains set on two dogs, as spill increased from 95 kcfs to 200 kcfs.  With the outage at PH2, several fish facilities lost power as well.

    - The DSM2 orifices closed, the STSs stopped traveling and the ERG tripped open.  The add-in water came on for 30 minutes but some fish were stranded in the two-mile pipe.  A memo from Project Fisheries was sent on 29 April.  Power was restored to DSM2 around 1610, at which time the ERG was closed and orifices returned to normal operation.

    - The JMF lost power.  The upper switchgate moved to the bypass position.  The lower switchgate remained in the high outfall position.  The PIT tag detectors lost power.  AWS flow continued.  Power returned to the JMF around 1600.

    - The B2CC remained open, but the PIT tag detector may have lost power.

    - Washington Shore attraction flow was off until F1 returned to service at 1540.  The entrance gates, already in manual, remained set at whatever elevation they were at.  SLADDs were off.

    - The AFF remained in trapping mode until station service was returned around 1430.

    - The Main Dam, Bradford Island and PH1 fishways remained in normal operation.

  - A teletype sent on 01 May requests PH2 units operate at the lower end of 1% to facilitate the safe passage of 4.77 million tule fall chinook released on 01 May.  The following actions occur in the order below:

    - Beginning at 0600 on 02 May and ending at 0559 on 10 May, operate PH2 units between the low end and lower quarter point of the 1% efficiency range (approximately 11.2 to 13.2 kcfs).  During this operation, PH2 units should be operated at about 50 MW.  If it is necessary to put the units on local control to achieve these targets, the Control Room should notify BPA and Real Time scheduling prior to going to local control.

    - PH1 units shall be operated within the 1% efficiency range.

    - If more generation is needed to avoid spilling over the gas cap, bring PH1 to full load then increase the PH2 units to the mid-range of 1% (approximately 15 kcfs) one unit at a time.

    - If more generation is still needed, increase PH2 units to full capacity (within the 1% efficiency range) one unit at a time.

    - If required, increase spill as necessary.

JAMES R. MAHAR, P.E.

Operations Manager