### CENWP-OD-B																								05 July 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 27 of 2009, which covers the period from 28 June through 04 July 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 140.0 to 253.2 kcfs.  Daily average project tailwater ranged from 12.8’ to 20.1’ msl.  Daily average powerhouse forebay elevation ranged from 74.8’ to 76.3’ msl.  Daily average river temperature ranged from 64ºF to 66ºF.  Secchi disk measurements ranged from 3.6’ to 6.0’.

  - Daily average spill ranged from 93.7 to 99.8 kcfs.

    - Spillbay 17 remains on two dogs (2.9’).  The bay should be at 3.5’ but due to a broken hoist it has to be dogged instead.  Flow is compensated through adjacent bays.

    - Spillbay 2 was flushed for debris from 0851 until 0926 on 01 July.

    - Spillbay 18 was flushed for debris from 0820 until 0851 on 01 July.

  - Unit Operation.  Powerhouse 2 remains the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 15 was out of service from 1036 until 1349 on 29 June for governor oil pressure switch repairs.

    - Unit 16 has remained out of service since 09 May due to exciter troubles and a grounding issue.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F2 was out of service from 2153 on 01 July until 0352 on 02 July for lamprey testing.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV3-7 was closed for cleaning from 1318 until 1330 on 01 July.

    - FV3-9 was closed for cleaning from 1034 until 1106 on 29 June.

    - FV4-3 and 4-4 were closed for Bay 18 flushing from 0820 until 0851 on 01 July.

    - FV 5-3 and 5-4 were closed for Bay 2 flushing from 0851 until 0926 on 01 July.

    - FV 5-9 was closed for cleaning from 0725 until 0735 on 29 June and from 1250 until 1300 on 01 July.

    - FV6-9 was closed for cleaning from 0705 until 0713 on 29 June and from 1250 until 1300 on 01 July.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1-2 | NA | NA | Remains out of service until 03 September. |
| 11 | NA | NA | Currently out of service |
| 16 | NA | NA | STSs removed on 15 June. |
| 12-15, 16-18 | 6/29, 7/1 | NA | All VBSs cleaned. |

2.2.1	Dewatering and Fish Salvage.  No fish salvage or dewatering activities occurred this week.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Reported a dead chinook on 29 June.  A memo was sent out on 02 July.

  - CRITFC- JMF video.  Waiting on new equipment for monitoring juvenile fish passage.

  - CTUIR.  No lamprey collected for radio- tagging from the AFF this week.  Total of 40 lamprey collected for 2009.

  - NOAA-FGE.  Test releases of PIT-tagged run of the river fish continued this week to assess passage conditions at two turbine operating ranges (middle and upper end of the 1% efficiency range).  2931 sub-yearling chinook were collected at the JMF.

  - NOAA Lamprey.  Trapping lamprey at the AFF for passage evaluations.

  - NOAA- pathogens. Determination of pathogen prevalence in juvenile salmonids.  26 sub-yearling chinook were collected at the JMF.

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - PNNL- BGS.  All hydrophones are installed and collecting data for the BGS evaluation.

  - PSMFC- Smolt monitoring.  Daily condition and index monitoring continues.  Fallbacks recorded crossing the separator bars included; four steelhead and four salmon.  Gas Bubble Trauma (GBT) exams occur twice a week; see www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  2931 sub-yearling chinook were collected for the FGE testing and 26 sub-yearling chinook were collected for pathogen testing.

  - WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways. Nighttime video counts began 15 June.

  - USDA Wildlife Services. Avian hazing continues.

  - University of Idaho.  Tagging adult chinook and lamprey for evaluation of the Cascades Is. entrance weir.

- FISHWAYS

  - Project biologists inspected 28 June through 02 July, 04 July.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| 7/3 | BON Project | No inspection | Lack of personnel |  |  |
| Once | BON Project | No calibration | Lack of personnel |  |  |
| BRADFORD ISLAND (BI) --Nothing to report |  |  |  |  |  |
| CASCADES ISLAND (CI)--Nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 6/29, 7/2 | Entrances | <13.0’ opening | In manual | Operators adjusted. |  |
| ITS |  |  |  |  |  |
| All week | Chain gates | Gates not set correctly | Gates in manual. | Please see 4.6.1. |  |
| DSM2/ JMF- nothing out of criteria |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

    - CI south entrance gate remains broken and closed.  It is been OOS since 10 April.  It will remain in the closed position for all tailwater elevations during the modified entrance evaluation.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington Shore.

    - The WS and BI probes have been sent to the manufacturer to be calibrated.  The AFF probe is being used as a surrogate.

Table 3.  Bonneville Fishway Temperatures

| Date | AFF average |
| --- | --- |
| 6/28 | 62.8 |
| 6/29 | 63.4 |
| 6/30 | 63.4 |
| 7/01 | 63.7 |
| 7/02 | 64.3 |
| 7/03 | 65.1 |
| 7/04 | 65.5 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was not checked this week due to a lack of personnel.

    - The Washington Shore fishway entrances are in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  The last gate was removed for maintenance and replaced with a bulkhead.

    - All adult fishways are operating in shad passage criteria.

  - Juvenile Fishways.

    - The PH1 ITS was closed for debris removal on 17 June.  To provide the best flow possible until the new gates can be automated, the chaingates were set as follows:  1B- 71’msl, 3B- 70’ msl, 6C- 70’msl, and 9A- 72’.

  - Lamprey Fishways.

    - The CI entrance weir and bulkhead slot filler are installed.

    - All lamprey passage structures remain watered-up.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal is scheduled for FY10.  Old DSM bypass equipment in the tailrace is scheduled for removal in FY10 as well.

    - The Program Logic Control (PLC) for the automated gates has not been completed.

    - The keeper pin for gate 3B needs to be replaced.  The Project plans to do this on 14 July when flows have dropped enough to no longer require units to operate at PH1.

  - TIE crane.  The new boom is to arrive in mid-July.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 17 May and revised on 18 May provides guidance for voluntary and involuntary spill by project as well as spill caps per project for various total dissolved gas (TDG) levels.

  - A teletype sent on 19 June requests the summer spill operations starting at 0001 on 21 June.  From 21 June until 2400 on 20 July, the Project will spill approximately 85 kcfs during daytime hours and to the 120% gas cap at night.  From 0001 on 21 July until 2400 on 31 August, the Project will spill approximately 75 kcfs during the day and up to the 120% gas cap at night.

  - A teletype sent on 26 June requests that from 0600 on 30 June until 1800 on 02 July, the forebay elevation be maintained at 75.0’ – 76.5’ msl. as a hard constraint and 75.5’ – 76.5’ msl. as a soft constraint.  This operation is requested to reduce debris in tribal fishing nets, reduce entanglement of fishing nets, minimize boat access problem, and reduce the chances of nets being torn from their anchors by limiting pool fluctuation.

  - A teletype sent on 29 June requests that from 2000 until 2300 hours on 04 July the forebay elevation be maintained at 75.8’-76.5 msl as a hard constraint and 76.0’-76.5’ msl as a soft constraint.  This operation is for Hood River’s fireworks show and public safety.

  - A teletype sent on 01 July requests the Project flush large wood from each end of the spillway before 1700 on 01 July.

JAMES R. MAHAR, P.E.

Operations Manager