### CENWP-OD-B																							13 September 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 37 of 2009, which covers the period from 06 through 12 September 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 71.1 to 93.4 kcfs.  Daily average project tailwater ranged from 7.2’ to 8.9’ msl.  Daily average powerhouse forebay elevation ranged from 75.4’ to 77.3’ msl.  Daily average river temperature ranged from 69ºF to 71ºF.  Secchi disk measurements 7.0’ all week.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.5 to 1.6 kcfs.

  - Unit Operation.  Unit priority has changed due to fish numbers requiring the Project to split flows.

    - Unit 1 was placed in service at 1207 on 08 September as per the teletype detailed in 7.6.

    - Unit 6 returned to service, having been out of service since 13 July for a five year overhaul, at 0957 on 09 September.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 16 has remained out of service since 09 May due to exciter troubles and a grounding issue.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was on reduced load from 2151 on 06 September until 0402 on 07 September.

    - F2 was on standby, or reduced load, for lamprey testing from: 2151 on 06 September until 0402 on 07 September; 2154 on 07 September until 0406 on 08 September; 2203 on 09 September until 0358 on 10 September.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following  AWS valves were closed this reporting week:

    - FV3-7 was closed for cleaning from: 0656 until 0840 on 10 September.

    - FV3-9 was closed for cleaning from: 0658 until 0715 on 08 September; 0656 until 0840 on 10 September.

    - FV5-9 was closed for cleaning from: 0656 until 0840 on 10 September.

    - FV6-9 was closed for cleaning from: 0656 until 0840 on 10 September.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1-2 | NA | NA | Scheduled for the week of 21 September. |
| 11, 16 | NA | NA | Out of service |
| 12-15, 17-18 | NA | NA | Scheduled for week of 21 September. |

    - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Daily average temperatures dropped below 69.5ºF on 07 September and normal trapping operations resumed.

  - CRITFC- JMF video.  New video equipment installed for monitoring juvenile fish passage.

  - NOAA Lamprey.  Trapping lamprey at the AFF for passage evaluations concluded on 04 September.

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - NWW truck release site.  Trucking and release at BON began on 16 August; continues every other day.

  - PSMFC- Smolt monitoring.  Modified sampling protocols due to elevated river temperature occurred this week.  One steelhead and one salmon were observed crossing the separator bars.  Gas Bubble Trauma (GBT) exams occur twice a week; see www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  No fish were held for researchers this week.

  - WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways. Nighttime video counts began 15 June.

  - WDFW Tule counts.  Tule counting continues.

  - USGS Shad.  Collecting juvenile shad from the Juvenile Fish Monitoring Facility for ongoing research on impacts of American Shad on the Columbia River.  No shad collected this week.

- FISHWAYS

  - Project biologists inspected 06 through 12 September.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 9/8 | B-branch diffusers | Incorrect diffusers for TW elevation. | PLC out of service | Operators manually adjusted diffusers. |  |
| 9/8 | B-branch entrance | High differential | Too many diffusers open | Operators adjusted. |  |
| 9/12 | A-branch weir | Reading >1.0’ | High forebay | No action taken. |  |
| CASCADES ISLAND (CI) nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) nothing to report |  |  |  |  |  |
| PH1 ITS – please see 4.5.7 |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder; the return ladder at the Adult Fish Facility (AFF); and the general holding tank at the Juvenile Monitoring Facility (JMF).

    - Three out of four temperature probes are experiencing technical difficulties.  Please see www.nwd-wc.usace.army.mil/tmt/documents/ops/temp/200909.lcol.html for additional temp data.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg | AFF Avg | JMF Avg |
| --- | --- | --- | --- | --- |
| 9/06 | NA | 69.1 | NA | NA |
| 9/07 | NA | 68.5 | NA | NA |
| 9/08 | NA | 68.1 | NA | NA |
| 9/09 | NA | 68.0 | NA | NA |
| 9/10 | NA | 68.3 | NA | NA |
| 9/11 | NA | 68.5 | NA | NA |
| 9/12 | NA | 68.4 | NA | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 11 September.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.

    - The Bradford Island exit was closed for cleaning from: 0658 until 0715 on 08 September; 0656 until 0840 on 10 September.

    - FV4-3 remains in manual.

    - DSM1 continues to head south.  STSs are in Units 1 and 2.  Orifice lights are on in those units as well.  Orifices are open for units 3-9.

      - Unit 10 orifices had to be closed at 1451 on 08 September due to high channel elevations, which was a result of the higher than normal forebay.

      - STSs and VBS will be pulled, and DSM1 dewatered, starting on 19 October to facilitate the ITS wall removal contract.

    - Chaingates are not set to FPP criteria.  The Project is testing gate configurations to optimize flow through the ITS.  The Project will monitor forebay elevations and manually adjust automated gates 3B and 6C to maintain >2.5’ depth.  Chaingate 10B is closed until ITS capacity is increased with wall removal.  9A is open and set at approximately 72’ msl.

  - Juvenile Fishways.

    - The B2CC remains closed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and bulkhead slot filler are installed.

    - The CI LPS and PH2 NDE ramp are dewatered for the season.

    - The Bradford Is. ladder AWS LPS and WA shore ladder AWS LPS remain watered-up.

- CONSTRUCTION

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall scheduled for removal in FY10.

    - The Program Logic Control (PLC) for the automated gates has not been completed.

  - TIE crane.  The crane is scheduled to be available by the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.

  - A teletype sent on 27 July changes the unit operation for PH2.  PH2 units will operate at the low end to mid point of the 1% efficiency range.

  - A teletype sent on 07 September requests the forebay be operated at 76.0’ – 77.5’ msl as a soft constraint from 0600 on 08 September until 1800 on 12 September.  This action is to limit pool fluctuation, during tribal fishing, to: reduce local currents that sweep debris into tribal fishing nets; reduce rapid water level changes that entangle nets; minimize boat access problems; avoid tearing nets from their anchors.

    - An extension and modification was requested in a teletype sent on 11 September.  It requests the forebay be operated at 76.0’ – 77.5’ msl as a hard constraint and 76.5’ – 77.5’ as a soft constraint from 0600 on 14 September until 1800 on 18 September.

  - Teletype sent on 28 August requests outflows from BON and TDA do not exceed 150 kcfs and remain as low and constant as possible from 0700 until 1130 on 07 September.  This request is to reduce river currents during the cross channel swim at Hood River.

    - This request was modified with a teletype sent on 09 September, which requests the forebay be maintained as steady as possible between elevation 76.0’ and 77.5’ msl from 0800 until 1000 on 12 September.  This modification was to comply with the Treaty fishing teletype detailed in 7.3.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010.

    - From 07 November through 31 December, 78.0’ msl will occur as needed to support chum spawning below the dam.

    - This requested operation is a deviation from the Bonneville Water Control Manual.  The deviation was coordinated with the Region on 21 August.

    - This operation is requested to facilitate TDA spillwall work.  If the spillwall construction is completed early, a return to normal forebay operating elevations will be coordinated.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) first.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

JERRY CARROLL

Acting Operations Manager