### CENWP-OD-B																							25 October 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2009, which covers the period from 18 through 24 October 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 74.4 to 104.9 kcfs.  Daily average project tailwater ranged from 7.4’ to 10.1’ msl.  Daily average powerhouse forebay elevation ranged from 77.1’ to 77.3’ msl.  Daily average river temperature remained 59ºF.  Secchi disk measurements ranged from 6.8’ to 7.0’ all week.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.3 to 1.4 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 was out of service from 2236 on 19 October until 1315 on 21 October for semi-annual maintenance.

    - Unit 1 was out of service from 0740 until 1101 on 19 October to facilitate STS and VBS removal.

    - Unit 2 was out of service from 1101 until 1430 on 19 October to facilitate STS and VBS removal.

    - Unit 4 has remained out of service since 14 September 2009 for five-year overhaul.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 17 has remained out of service since 05 October for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week:

    - FV3-7- from 0954 until 1006 on 20 October.

    - FV3-9- from 0954 until 1006 on 20 October.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1 | 10/19 |  | STSs and VBSs removed |
| 2 | 10/19 |  | STSs and VBSs removed. |
| 11, 16 | NA | NA | Out of service |
| 12-15, 17-18 | 10/22 | NA | All VBSs cleaned. STS inspection scheduled for the week of 26 October. |

    - Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week:

      - On 19 October, Fisheries removed four crawdads and one sculpin from DSM1.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF concluded on 21 October.

  - CRITFC- JMF video.  New video equipment installed for monitoring juvenile fish passage.

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - NWW truck release site.  Trucking and release at BON began on 16 August; continues every other day.

  - PSMFC- Smolt monitoring.  Daily condition and index monitoring continues.  Two steelhead and 15 salmon were observed crossing the separator bars.  Gas Bubble Trauma (GBT) exams occur twice a week; see www.fpc.org/CurrentDaily/Gbtsum.txt for further details.   Monitoring will conclude at 0700 on 30 October.

  - USGS- Didson testing.  Didson camera deployed in UMT on 22 October for approximately one hour.

  - WDFW Fish Counting.  Visual counting continues at Bradford Island and Washington Shore fishways.

- FISHWAYS

  - Project biologists inspected 18 through 24 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) nothing to report |  |  |  |  |  |
| CASCADES ISLAND (CI) nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) nothing to report |  |  |  |  |  |
| PH1 ITS – please see 4.5.6 |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 09/10.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.

    - Three out of four temperature probes are experiencing technical difficulties.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg |
| --- | --- | --- |
| 10/18 | NA | 58.0 |
| 10/19 | NA | 58.2 |
| 10/20 | NA | 58.3 |
| 10/21 | NA | 58.3 |
| 10/22 | NA | 58.0 |
| 10/23 | NA | 57.7 |
| 10/24 | NA | 57.2 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 23 October.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.

    - FV4-3 remains in manual due to a defective conduit sensor.  Repairs scheduled for 09/10.

    - DSM1 went out of service and was dewatered at 1400 on 19 October.  Remaining fish screens were removed and scrapped.

    - Chaingates are not quite to FPP criteria.  Automated gates 3B and 10B are manually set to 2.5’.  Automated gate 6C still is not working properly.  Chain gate 6B has been opened to maintain at least 2.5’ opening.  With the high forebay, 1B has been closed and 1C opened to 72’ msl.

      - The ITS is scheduled to be dewatered on 02 November, to facilitate the ITS wall removal contract.

  - Juvenile Fishways.

    - The B2CC remains closed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and bulkhead slot filler remain installed.

    - The CI LPS and PH2 NDE ramp are dewatered for the season.

    - The BI and WS AWS LPSs remain watered-up.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails scheduled for replacement in FY10.  New crane in FY11.  Contractors will begin work on the +55 deck starting 02 November.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall scheduled for removal in FY10.

    - The Program Logic Control (PLC) for the automated gates has not been completed.

  - TIE crane.  The crane is scheduled to be available by the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.

  - A teletype sent on 27 July changes the unit operation for PH2.  PH2 units will operate at the low end to mid point of the 1% efficiency range.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010.

    - From 07 November through 31 December, 78.0’ msl will occur as needed to support chum spawning below the dam.

    - This requested operation is a deviation from the Bonneville Water Control Manual.  The deviation was coordinated with the Region on 21 August.

    - This operation is requested to facilitate TDA spillwall work.  If the spillwall construction is completed early, a return to normal forebay operating elevations will be coordinated.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - Teletype sent on 15 October requests that from 0900 until 1600 on 27 October, the tailrace elevation remain within a one foot range, as a soft constraint.  In addition, spill bay 1 may be closed from 1145 until 1345 and spill bay 18 may be closed from 1315 until 1415.  The purpose of this request is to maintain a constant tailwater elevation to conduct velocity and flow measurements at Cascades Island and reduce water turbulence during the stilling basin survey.

  - A teletype sent on 21 October requests discharge flows remain between 110 and 120 kcfs, as a soft constraint, from 2200 until 2400 on 21 October.  This is to aid the egress of the naval  vessel “The Sea Fighter”, which has been dry docked at the Portland Harbor.

    - A teletype sent later on 21 October modified the teletype in 7.6.  The new request is for flows as high as possible from 0900 until 1100 on 22 October.

  - Winter maintenance schedules are available from Project Fisheries.

JERRY CARROLL

Acting Operations Manager