### CENWP-OD-B																							08 November 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 45 of 2009, which covers the period from 01 through 07 November 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 95.1 to 121.3 kcfs.  Daily average project tailwater ranged from 9.3’ to 11.5’ msl.  Daily average powerhouse forebay elevation ranged from 77.0’ to 77.5’ msl.  Daily average river temperature ranged from 53 to 55ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged between 1.1 to 1.2 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 3 was out of service from 0628 on 01 November until 0926 on 02 November due to the main breaker not closing.

    - Unit 4 returned to service at 1408 hrs on 5 November. It had been out of service since 14 September 2009 for five-year overhaul.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 went out of service at 1415 on 05 November to facilitate DSM1 orifice removal.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 17 has remained out of service since 05 October for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F2 was at reduced load from 0748 until 1233, then out of service from 1233 until 1423, on 05 November to facilitate trashrack raking.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week:

    - FV1-1- Closed for cleaning from 1322 until 1335 on 05 November.

    - FV3-7- Closed for cleaning from 0957 until 1007 on 03 November and from 1027 until 1040 on 05 November; placed in manual from 0839 until 1540 on 04 November to facilitate the re-routing of a communication cable.

    - FV3-9- Closed for cleaning from  0957 until 1007 on 03 November and from 1027 until 1040 on 05 November.

    - FV5-9- Closed for cleaning from 1002 until 1010 on 05 November.

    - FV6-9- Closed for cleaning from 1015 until 1025 on 05 November.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.  Report 0944 listed the incorrect date of inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 2 | NA |  | STSs and VBSs removed |
| 11 | NA |  | Out of service |
| 12 | 10/29 | 789 | OK |
| 13 | 10/29 | 604 | OK |
| 14 | 10/29 | 781 | OK |
| 15 | 10/29 | 789 | OK |
| 16 | NA | 360 | OK |
| 17 | 10/29 |  | Out of service |
| 18 | 10/29 | 788 | OK |

    - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week:

- RESEARCH

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - NWW truck release site.  Trucking and release at BON began on 16 August.  Trucking operations continue to take place on an every other day basis from Little Goose and Lower Monumental.

  - WDFW Fish Counting.  Video counting began at Bradford Island and Washington Shore fishways on 01 November.

- FISHWAYS

  - Project biologists inspected 01 through 07 November

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/2 | A-branch weir | Reading >1.0’< | Unknown | Self corrected. |  |
| CASCADES ISLAND (CI) nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 11/7 | FG6-18 | Incorrect position | TW deadband | Self corrected |  |
| 11/7 | A/B diffusers | Incorrect position | Manually operated | Ops corrected. |  |
| 11/5 | WS monoliths | Entrance differential low. | F2 OOS for trashraking | Back to normal by 1423 |  |
| PH1 ITS – please see 4.5.5 |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.

    - Three out of four temperature probes are experiencing technical difficulties.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg |
| --- | --- | --- |
| 11/01 | NA | 53.8 |
| 11/02 | NA | 53.6 |
| 11/03 | NA | 53.4 |
| 11/04 | NA | 52.9 |
| 11/05 | NA | 52.7 |
| 11/06 | NA | 52.8 |
| 11/07 | NA | 52.8 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 06 November.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.

    - FV4-3 remains in manual due to a defective conduit sensor.  Repairs scheduled for 09/10.

    - Chaingates are not quite to FPP criteria.  Automated gates 3B and 10B are manually set to 2.5’.  Automated gate 6C still is not working properly.  Chain gate 6B has been opened to maintain at least 2.5’ opening.  With the high forebay, 1B has been closed and 1C opened to 72’ msl.

      - The ITS chain and automated gates were closed and bulkheaded this week.  The ITS has been dewatered to facilitate the wall removal contract.

    - The Bradford Island exit was closed for cleaning from 0957 until 1007 on 03 November and from 1027 until 1040 on 05 November.

  - Juvenile Fishways.

    - The B2CC remains closed.

    - DSM1 remains dewatered.  Wall and orifice removal continues.

    - The hydrocannon was shut off and winterized at 1448 on 02 November.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and bulkhead slot filler remain installed.

    - The CI LPS and PH2 NDE ramp are dewatered for the season.

    - The BI and WS AWS LPSs were dewatered on 04 November.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails scheduled for replacement in FY10.  New crane in FY11.  Contractors will begin work on the +55 deck starting 02 November.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall scheduled for removal in FY10.

  - TIE crane.  The crane is scheduled to be available by the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.

  - A teletype sent on 27 July changes the unit operation for PH2.  PH2 units will operate at the low end to mid point of the 1% efficiency range.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010.

    - From 07 November through 31 December, 78.0’ msl will occur as needed to support chum spawning below the dam.

    - This requested operation is a deviation from the Bonneville Water Control Manual.  The deviation was coordinated with the Region on 21 August.

    - This operation is requested to facilitate TDA spillwall work.  If the spillwall construction is completed early, a return to normal forebay operating elevations will be coordinated.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.  All constraints outlined in 7.3 should be followed as well.

    - If needed, BON is authorized to pass water in excess of what is necessary to meet the 11.3’ hard constraint by increasing tailwater elevation to 18.5’ msl between 1700 and 0600 hours.  Normal ramp rates still apply and the constraints in 7.3 should still be met.

    - If the actions in 7.5.1 are not sufficient, tailwater elevations may increase, as necessary, up to 12.5’ msl between 0600 and 1700 hours, daily.

    - The official tailwater gauge is located at river mile 144.5, on the Oregon shore.

    - BON is requested to coordinate closely with BPA to achieve the requested tailwater constraints.  It is recognized that tidal effects, wind and lower river flows may impact the ability to maintain the requested operation.

JERRY CARROLL

Acting Operations Manager