### CENWP-OD-B																							15 November 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 46 of 2009, which covers the period from 08 through 14 November 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 119.3 to 138.0 kcfs.  Daily average project tailwater ranged from 11.5’ to 12.8’ msl.  Daily average powerhouse forebay elevation ranged from 76.3’ to 77.2’ msl.  Daily average river temperature was 53ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill was 1.2 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 3 was out of service from 1657 until 1832 on 09 November due to a trip on A-phase differential.

    - Unit 4 was out of service from 1657 until 1838 on 09 November due to a trip on A-phase differential.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 returned to service at 1420 on 14 November.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 17 has remained out of service since 05 October for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week:

    - FV3-9- Closed for cleaning from 1024 until 1042 on 12 November.

    - FV5-9- Closed for cleaning from 1045 until 1100 on 12 November.

    - FV6-9- Closed for cleaning from 1045 until 1100 on 12 November.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.  Report 0944 listed the incorrect date of inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 2 | NA |  | STSs and VBSs removed |
| 11, 16 | NA |  | Out of service |
| 12-15, 17-18 | NA | NA | Next inspections scheduled for late November. |

    - Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week:

      - On 09 November, Project Fisheries removed three unknown salmon and three unknown origin steelhead from the AFF entrance and exit.  Fisheries removed three unknown origin steelhead from under the brail pool.  Five sturgeon were herded to the Washington Shore.  All fish were released downstream.

- RESEARCH

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - NWW truck release site.  Trucking and release at BON began on 16 August.  Trucking operations concluded for the season.

  - WDFW Fish Counting.  Video counting at Bradford Island and Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 08 through 14 November

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/8-9 | A-branch weir | Reading >1.0’ | Unknown | No action. |  |
| 11/9 | PH1 S entrance | Differential < 1.0’ | Unknown | Ops adjusted. |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |
| 11/9 | CI entrance | Differential >2.0 | Sensor issues | FV5-3 & 5-4 in manual. See 4.5.5 | 10-25315 |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| PH1 ITS – currently under construction |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.

    - Three out of four temperature probes are experiencing technical difficulties.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg |
| --- | --- | --- |
| 11/08 | NA | 52.5 |
| 11/09 | NA | 52.5 |
| 11/10 | NA | 52.3 |
| 11/11 | NA | 52.4 |
| 11/12 | NA | 52.2 |
| 11/13 | NA | 51.9 |
| 11/14 | NA | 51.5 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 11 November.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.

    - FV4-3 remains in manual due to a defective conduit sensor.  Repairs scheduled for 09/10.

    - FV5-3 and FV5-4 were placed in manual on 09 November due to a tailwater sensor calibration issue.  Repairs scheduled for next week.

    - The ice and trash sluiceway ( ITS) remains dewatered.

  - Juvenile Fishways.

    - The B2CC remains closed.

    - DSM1 remains dewatered.  Wall and orifice removal continues.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All lamprey passage structures (LPSs) have been dewatered.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails scheduled for replacement in FY10.  New crane in FY11.  Contractors began work on the +55 deck on 02 November.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall removal underway.

  - TIE crane.  The crane is scheduled to be available by the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July until U11 returns to service.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.

JERRY CARROLL

Acting Operations Manager