### CENWP-OD-B																							29 November 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 48 of 2009, which covers the period from 22 through 28 November 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 109.4 to 126.3 kcfs.  Daily average project tailwater ranged from 11.5’ to 11.7’ msl.  Daily average powerhouse forebay elevation ranged from 76.0’ to 76.9’ msl.  Daily average river temperature ranged between 49ºF to 50ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.1 to 1.2 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 3 has remained out of service since 19 November due to a loss of Bank 3/4.

    - Unit 4 has remained out of service since 19 November due to a loss of Bank 3/4.

    - Unit 6 has remained out of service since 21 November for DSM1 orifice removal.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 10 has remained out of service since 16 November for DSM1 orifice removal.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 17 has remained out of service since 05 October for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed for cleaning this reporting week:

    - FV1-1- Closed for cleaning from 1327 until 1350 on 23 November.

    - FV3-7- Closed for cleaning from 1327 until 1333 on 23 November.

    - FV3-9- Closed for cleaning from 1327 until 1333 on 23 November.

    - FV6-9- Closed for cleaning from 1327 until 1342 on 23 November.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 2 | NA |  | STSs and VBSs removed |
| 11 | NA |  | Out of service |
| 12 | 11/23 | 674 | VBSs cleaned on 25 November. |
| 13 | 11/23 | 672 | OK |
| 14 | 11/23 | 674 | OK |
| 15 | 11/23 | 665 | OK |
| 16 | 11/23 | 613 | OK |
| 17 | NA |  | Out of service |
| 18 | 11/23 | 674 | VBSs cleaned on 25 November. |

    - Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week:

      - On 24 November, Fisheries removed 52 sculpin, two crawdads, one catfish, and one sturgeon from U17 taillogs.  Fish were released downstream.

- RESEARCH

  - NOAA- PIT tag detectors.  Vibration sensors remain installed on Spill bay 6.

  - ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.

  - Smith-Root sea lion array.  Array installation scheduled for 02 December in the UMT.

  - WDFW Fish Counting.  Video counting at Bradford Island and Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 22 through 28 November.  NOAA inspected on 25 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/22 | BI Weir | Reading <1.0’ | Unknown | Self corrected. |  |
| 11/22-23 | BI Exit | Needs cleaning. | Excessive debris | Riggers cleaned. |  |
| 11/25 | A-branch weir | Reading >1.0’ | Unknown | No action. |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS)- nothing to report |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.

    - Three out of four temperature probes are experiencing technical difficulties.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg |
| --- | --- | --- |
| 11/22 | NA | 49.1 |
| 11/23 | NA | 48.8 |
| 11/24 | NA | 49.0 |
| 11/25 | NA | 48.8 |
| 11/26 | NA | 48.5 |
| 11/27 | NA | 48.3 |
| 11/28 | NA | 48.1 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 26 November.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

    - There are currently 11 of 12 floating orifice gates (FOG) installed at Powerhouse 2.  One gate was removed for maintenance and replaced with a bulkhead.

    - FV4-3 remains in manual due to a defective conduit sensor.  Repairs scheduled for 09/10.

    - The PH1 ice and trash sluiceway (ITS) remains dewatered.

    - The Bradford Island fish exit was cleaned on 23 November.

  - Juvenile Fishways.

    - The B2CC remains closed.

    - DSM1 wall and orifice removal continues.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.

    - All lamprey passage structures (LPSs) have been dewatered.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall and DSM1 outfall removal continues.

  - TIE crane.  The boom was attached on 24 November.  Crane is scheduled to be load tested the week of 29 November.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.

JERRY CARROLL

Acting Operations Manager