### CENWP-OD-B																							20 December 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 51 of 2009, which covers the period from 13 through 19 December 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 113.4 to 140.5 kcfs.  Daily average project tailwater ranged from 11.5’ to 13.4’ msl.  Daily average powerhouse forebay elevation ranged from 75.6’ to 76.4’ msl.  Daily average river temperature stayed at 42ºF.  Secchi disk measurements ranged from 4.0’ to 6.5’.

  - Spill Bays 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.6 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 2 went out of service at 1419 on 14 December for DSM1 orifice removal.

    - Unit 5 returned to service, after being out since 04 December, at 1414 on 14 December.  Unit 5 was out of service from 1701 until 1735 on 15 December due to Bank 7/8 tripping offline.  Unit 5 was out of service from 0724 until 1220 on 17 December due to relay setting change on Bank 5/6 differential.

    - Unit 6 was out of service from 1701 until 1733 on 15 December due to Bank 7/8 tripping offline.  Unit 6 was out of service from 0724 until 1220 on 17 December due to relay setting change on Bank 5/6 differential.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 8 was out of service from 1701 until 1732 on 15 December due to Bank 7/8 tripping offline.  Unit 8 was out of service from 0758 until 1426 on 16 December due to Bank 7/8 relaying.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 10 was out of service from 0510 until 0752 on 18 December due to exciter trouble.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0100 on 14 December until 1406 on 15 December for station service switchgear replacement and turbine bearing repair.  STSs were removed at this time as well.

    - Unit 13 was out of service from 0054 until 1525 on 14 December to facilitate station service switchgear replacement on Unit 14.  Unit 13 was out of service from 0659 until 0900 on 17 December for STS removal.

    - Unit 14 was out of service from 0050 on 14 December until 1433 on 15 December for station service switchgear replacement and turbine bearing repair.  STSs were removed at this time as well.

    - Unit 15 was out of service for STS removal from 1357 until 1608 on 16 December; 0940 until 1609 on 17 December; 0617 until 0850 on 18 December.

    - Unit 16 was out of service from 0952 until 1354 on 16 December for STS removal.

    - Unit 17 was out of service from 0703 until 0948 on 16 December for STS removal.

    - Unit 18 was out of service from 0654 until 1003 on 15 December for STS removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 remains out of service for annual maintenance.

    - F2 was out of service from 0300 until 0904 on 15 December because the breaker would not close.  F2 was out of service from 1300 until 1545 on 18 December for trashraking.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1, 3-7, 3-9, 4-3, and 4-4 remain closed for winter maintenance in Bradford Island.

    - FV5-9 was closed for cleaning from 1609 until 1624 on 18 December.

  - STS/VBS inspections.  The following STS/VBS inspections and removal occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1, 2 | NA | NA | STSs and VBSs scrapped on 19 October 2009 |
| 11 | NA | OOS | STSs removed on 28 August 2008. |
| 12 | 12/14 | 496 | STSs removed. |
| 13 | 12/17 | 560 | STSs removed |
| 14 | 12/14 | 495 | STSs removed |
| 15 | 12/18 | 596 | Attempted STS removal on 12/16. STSs stuck. Inspected on 12/17, found stick in STS, preventing it from folding in. Stick removed on 12/17 at 1608. STSs left in until 12/18. |
| 16 | 12/16 | 553 | STSs removed |
| 17 | 12/16 | 362 | STSs removed |
| 18 | 12/15 | 526 | STSs removed |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6.

  - ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.

  - Smith-Root sea lion array.  Array remains installed in the UMT.

  - WDFW Fish Counting.  Video counting at Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 14, 15, and 18 December.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI)- currently dewatered |  |  |  |  |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 12/15 | Unit 12 | Started w/o slow roll after 36 hrs | Operator error. | Please see 7.5 |  |
| 12/13-14 | PCC/monoliths | Head differential, entrances closed | No stab plates installed. | Stab plates installed 12/14 |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island; the junction of the UMT and the Washington Shore ladder.

    - Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WS Avg | BI Avg |
| --- | --- | --- |
| 12/1-2/28 | NA | NA |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 18 December.

    - The PH1 ice and trash sluiceway (ITS) remains dewatered.

      - The wooden bulkhead is scheduled for replacement this winter.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

      - PH2 north upstream entrance remains closed.  The other gates are adjusted to maintain a 13’ opening, as tailwater allows.

    - 11 of 12 floating orifice gates (FOG) remain installed at PH2.  One gate was removed for maintenance and replaced with a bulkhead.

      - Stab plate installation was completed at 1131 on 14 December.

  - Juvenile Fishways.

    - The B2CC remains closed.

    - DSM2 emergency relief gate was opened at 1000 on 19 December in preparation of the channel dewatering on 21 December.  The flume flushing valve and emergency pipe drain valve were opened at 0750 on 19 December.

  - Lamprey Fishways.  All LPSs remain dewatered.

    - The Cascades Is. entrance weir and slot filler remain installed.

    - The PH2 north downstream entrance ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal continues.  Outfall removal has been cancelled.

  - TIE crane.  Load testing occurred the week of 29 November.

- HAZMAT, SPILLS AND CLEANUP.   Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.

  - On 15 December, several on-site personnel reported seeing floating sturgeon after Unit 12 was put on-line.  There was no confirmation of any mortalities.  The unit had not been started by slow rolling, as per the FPP BON 5.7, to flush sturgeon out of the draft tube.  Control Room operators have corrected this situation.

JERRY CARROLL

Acting Operations Manager