### -CENWP-OD-B																							28 December 2009

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 52 of 2009, which covers the period from 20 through 26 December 2009.

- OPERATION SUMMARY

  - Daily average river flows ranged from 111.3 to 142.5 kcfs.  Daily average project tailwater ranged from 11.5’ to 13.0’ msl.  Daily average powerhouse forebay elevation ranged from 76.0’ to 76.4’ msl.  Daily average river temperature ranged between 38ºF and 42ºF.  Secchi disk measurements ranged from 5.0’ to 7.0’.

  - Spill Bays 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill ranged from 0.5 to 0.6 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 1 went out of service at 0740 on 21 December for DSM1 orifice removal.

    - Unit 2 returned to service, after being out since 14 December, at 1011 on 21 December.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 remains out of service for annual maintenance.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1, 3-7, 3-9, 4-3, and 4-4 remain closed for winter maintenance in Bradford Island.

    - FV5-9- closed for cleaning from 1600 until 1615 on 22 December.

    - FV6-9- closed for cleaning from 1615 until 1630 on 22 December.

  - STS/VBS inspections.  The following STS/VBS inspections and removal occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | STSs removed on 28 August 2008. |
| 12-18 | NA |  | STSs scheduled for installation the week of 21 February. |

  - Dewatering and Fish Salvage.  The following dewatering/fish salvage activities occurred this week.

    - Fisheries dewatered DSM2 on 21 December.  No fish were found.

- RESEARCH

  - NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6.

  - ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.

  - Smith-Root sea lion array.  Array remains installed in the UMT.

  - WDFW Fish Counting.  Video counting at Washington Shore continues.

- FISHWAYS

  - Project biologists inspected 20 through 23 December.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI)- fishway currently dewatered |  |  |  |  |  |
| 12/23 | PH1 turbines | U8 started, no slow roll | See 4.5.5 |  |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) – nothing to report |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 22 December.

    - The PH1 ice and trash sluiceway (ITS) remains dewatered.

      - The wooden bulkhead is scheduled for replacement this winter.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

      - NUE remains closed.  The other gates are adjusted to maintain a 13’ opening, as tailwater allows.

    - Stab plates remain installed in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Unit 8 was put online from 1805 on 23 December until 0202 on 24 December.  The unit could not be slow rolled due to a problem switching the governor to manual.

    - The Bradford Island fishway exit was surveyed from 1000 until 1100 on 21 December.  The survey was to determine how many cubic yards of sediment need to be dredged.

  - Juvenile Fishways.

    - The B2CC remains closed.

    - DSM2 Add-in valve was closed at 0938 on 21 December.  The channel was dewatered and walked by Fisheries shortly after that.  No fish were found.  The ERG will remain open until the DSM returns to service in late February.

  - Lamprey Fishways.  All LPSs have been dewatered.

    - The Cascades Is. entrance weir and slot filler remain installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal.  Wall removal continues.  Outfall removal has been cancelled.

  - TIE crane.  Load testing occurred the week of 29 November.

- HAZMAT, SPILLS AND CLEANUP.

  - An oil sheen was reported (NRC #926803, OERS  #2009-2924)at the south end of the PH1 tailrace at 1400 on 21 December.  Upon further investigation, it was determined to have originated with the ITS contractors.  One pint, or less, had been spilled.  Oil booms were in place and clean-up was completed by 1555 on 21 December.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 01 September requests BON forebay maintain 71.5’ to 78.0’ msl as a hard constraint and 71.5’ to 77.5’ as a soft constraint from 0001 on 08 September 2009 until 31 March 2010 to support chum spawning below the dam.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 05 November requests BON tailwater elevation hard constraint of no less than 11.3’ msl during all hours and a soft constraint of 11.3’ to 11.7’, with a target of 11.5’, from 0600 until 1700 daily.  This is effective from 0600 on 06 November until further notice.  This request is to provide necessary flows for chum spawning.

JERRY CARROLL

Acting Operations Manager