### CENWP-OD-B																							08 February 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 06 of 2010, which covers the period from 31 January through 06 February 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 114.7 to 120.7 kcfs.  Daily average project tailwater ranged from 11.6’ to 11.8’ msl.  Daily average powerhouse forebay elevation ranged from 76.2’ to 76.9’ msl.  Daily average river temperature ranged from 41 to 42ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bay 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill ranged from 0.6 to 0.7 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0702 until 0726 on 01 February for packing adjustment, and from 0747 until 1050 on 02 February for trash raking.

    - Unit 13 was out of service from 0807 until 0830 on 01 February for packing adjustment, and from 1047 until 1113 on 02 February for trash raking.

    - Unit 14 was out of service from 1115 until 1209 on 02 February for trash raking.

    - Unit 15 was out of service from 1307 until 1350 on 02 February for trash raking.

    - Unit 16 was out of service from 0907 until 0920 on 01 February for packing adjustment, and from 1355 until 1429 on 02 February for trash raking.

    - Unit 17 was out of service from 1014 until 1027 on 01 February for packing adjustment, and from 1502 until 1531 on 02 February for trash raking.

    - Unit 18 was out of service from 1541 until 1628 on 02 February, and from 0633 until 1053 on 03 February for trash raking.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 remains out of service for annual maintenance.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1, 3-7, 3-9, 4-3, and 4-4 remain closed for winter maintenance in Bradford Island.

    - FV5-9 was closed for cleaning from 0842 until 0902 on 02 February.

  - STS/VBS inspections.  The following STS/VBS inspections and removal occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | STSs removed on 28 August 2008. |
| 12-18 | NA |  | STSs scheduled for installation the week of 21 February. |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - FFU- sea lion.  Observations began on 08 January.  Weekly reports of sea lion activity will be available from Fisheries Field Unit starting in February. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6.

  - ODFW/WDFW sea lions.  Moved the forebay sea lion trap on 19 November.

  - Smith-Root sea lion array.  Array remains installed in the UMT. Testing is scheduled for 22 February.

  - WDFW Fish Counting.  Video counting at Washington Shore continues.

  - WDFW, ODFW, CRITFC.  Hazing of Steller sea lions has been occurring on a limited basis since mid-January.  Hazing of California sea lions will begin on 1 March.

- FISHWAYS

  - Project biologists inspected 01-03 February.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI)- fishway currently dewatered |  |  |  |  |  |
| CASCADES ISLAND (CI) – nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 2/3 | ##### PH2 entrances | ##### Differential <1.0’ | ##### Raking F2 | ##### Completed by 1200 |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 03 February.

    - The PH1 ice and trash sluiceway (ITS) remains dewatered.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

      - NUE remains closed.  The other gates are adjusted as needed.

    - Stab plates remain installed in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Sea Lion Exclusion Devices (SLEDs) were installed at the south end of PH1 on 22 January, and the B-branch entrance on 01 February.  SLEDs remain installed at PH2 and Cascades Island.

  - Juvenile Fishways.

    - The B2 Corner Collector remains closed.

    - DSM2 remains dewatered.  It is scheduled to be watered up the week of 22 February.

  - Lamprey Fishways.  All LPSs have been dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal continues.  Outfall removal has been postponed.

  - TIE crane.  TIES are scheduled to be installed for the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 08 January requests BON forebay maintain 71.5’ to 77.0’ msl as a soft constraint, and 71.5’ to 77.5’ msl as a hard constraint from 0001 on 09 January until 1800 on 31 March.  This is a modification of the 01 September teletype.  This request is to reduce the risk of flooding machinery and twisting bollards at BON locks, while still supporting spillwall construction at TDA.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 30 December requests BON tailwater elevation be maintained at no less than 11.5’ msl during all hours.  This is effective from 1600 on 30 December until further notice.  This request is to provide necessary flows for chum egg incubation.

JERRY CARROLL

Acting Operations Manager