### CENWP-OD-B																							16 February 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 07 of 2010, which covers the period from 07 through 13 February 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 118.7 to 125.1 kcfs.  Daily average project tailwater ranged from 11.6’ to 11.7’ msl.  Daily average powerhouse forebay elevation ranged from 75.7’ to 76.2’ msl.  Daily average river temperature was 42ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bay 1, which provides attraction flow for Cascades Island, is open 6” during daylight hours.  Daily average spill was 0.6 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0014 on 08 February until 1418 on 10 February for headgate removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 remains out of service for annual maintenance.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1, 3-7, 3-9, 4-3, and 4-4 remain closed for winter maintenance in Bradford Island.

    - FV5-9 was closed for cleaning from 0832 until 0852 on 09 February.

    - FV6-9 was closed for cleaning from 0832 until 0852 on 09 February.

  - STS/VBS inspections.  The following STS/VBS inspections and removal occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | STSs removed on 28 August 2008. |
| 12-18 | NA |  | STSs scheduled for installation the week of 21 February. |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - FFU- sea lion.  Observations began on 08 January.  Weekly reports of sea lion activity will be available from Fisheries Field Unit starting in February. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- PIT tag detectors.  Vibration sensor remains installed on Spill bay 6.

  - ODFW/WDFW sea lions.  Moved sea lion traps adjacent to B2CC on 11 February.

  - Smith-Root sea lion array.  Array remains installed in the UMT. Testing is scheduled for the week of 22 February.

  - WDFW Fish Counting.  Video counting at Washington Shore continues.

  - WDFW, ODFW, CRITFC Sea lion hazing.  Hazing of Steller sea lions has been occurring on a limited basis since mid-January.  Hazing of California sea lions will begin on 01 March.

- FISHWAYS

  - Project biologists inspected 09, 11, 12 February.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI)- fishway currently dewatered |  |  |  |  |  |
| CASCADES ISLAND (CI) – nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) – nothing to report |  |  |  |  |  |

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 2009/2010 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 12 February.

    - The PH1 ice and trash sluiceway (ITS) remains dewatered.  It is scheduled to be watered up prior to 01 March.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.

      - NUE remains closed.  The other gates are adjusted as needed.

    - Stab plates remain installed in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Sea Lion Exclusion Devices (SLEDs) remain installed at the south end of PH1, B-branch, PH2, and Cascades Island.  SLEDs will be installed at the north end of PH1 when bulkheads are removed.

  - Juvenile Fishways.

    - The B2 Corner Collector remains closed. Concrete repairs are complete, and concrete is curing.

    - DSM2 remains dewatered.  It is scheduled to be watered up on 18 February.

  - Lamprey Fishways.  All LPSs have been dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  Crane rails replacement continues.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal continues.  Outfall removal has been postponed.

  - TIE crane.  TIES are scheduled to be installed for the 2010 fish passage season.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 08 January requests BON forebay maintain 71.5’ to 77.0’ msl as a soft constraint, and 71.5’ to 77.5’ msl as a hard constraint from 0001 on 09 January until 1800 on 31 March.  This is a modification of the 01 September teletype.  This request is to reduce the risk of flooding machinery and twisting bollards at BON locks, while still supporting spillwall construction at TDA.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 30 December requests BON tailwater elevation be maintained at no less than 11.5’ msl during all hours.  This is effective from 1600 on 30 December until further notice.  This request is to provide necessary flows for chum egg incubation.

GLEN SMITH

Operations Manager