### CENWP-OD-B																							15 March 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 11 of 2010, which covers the period from 07 through 13 March 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 115.3 to 126.2 kcfs.  Daily average project tailwater was 11.4’ msl.  Daily average powerhouse forebay elevation ranged from 74.9’ to 76.5’ msl.  Daily average river temperature was 44ºF.  Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS valves were closed this reporting week.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 |  |  | STSs installed |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – Gatewell velocity testing.  Began on 11 March.

  - CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.

  - FFU- sea lion.  Observations continue.  Weekly reports of sea lion activities are now available. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- lamprey.  Cascades Island lamprey ramp camera remains installed.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  14 steelhead.  Please see http://www.fpc.org/adultsalmon/bonkeltcounts.htm for updated kelt counts.

  - Smith-Root- sea lion array.  Array remains installed in the UMT.  DIDSON installation to occur in late March.

  - WDFW- Fish Counting.  Video counting continues at WA shore and Bradford Island.

  - WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats continues.  Sea lion traps remain in position.  Trapping continues.

  - USDA Wildlife Services- Sea lion hazing.  Hazing from shore continues.

- FISHWAYS

  - Project biologists inspected 07-13 March.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI)- nothing to report |  |  |  |  |  |
| PH1 ICE AND TRASH SLUICEWAY |  |  |  |  |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) – nothing to report |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 3/7 | 42.6 | N/A |
| 3/8 | 42.6 | N/A |
| 3/9 | 42.4 | N/A |
| 3/10 | 42.5 | N/A |
| 3/11 | 42.4 | N/A |
| 3/12 | 42.3 | N/A |
| 3/13 | 42.2 | N/A |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 12 March.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances.

  - Juvenile Fishways.

    - The B2 Corner Collector is expected to open the morning of 14 March.  The 20 kelt trigger for opening B2CC was reached on 13 March.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains watered up.  The automated chain gates are open and in auto.  Chain gates 1A and 1B were open on 10 March to elevations 68’ msl and 72’ msl, respectively.  Fisheries will adjust these as necessary based on channel conditions and forebay.

    - Hydrocannon remains in service.

    - TIES remain installed.

    - 12A-S and 12A-N orifices were closed from 1002 until 1741 on 10 March to assist Battelle with removal of the ADV in U12 gatewell.

  - Lamprey Fishways.  All LPSs are dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal is complete.  Outfall removal has been postponed.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 08 January requests BON forebay maintain 71.5’ to 77.0’ msl as a soft constraint, and 71.5’ to 77.5’ msl as a hard constraint from 0001 on 09 January until 1800 on 31 March.  This is a modification of the 01 September teletype.  This request is to reduce the risk of flooding machinery and twisting bollards at BON locks, while still supporting spillwall construction at TDA.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 23 February replaces the teletype sent on 30 December.  It requests BON tailwater elevation be maintained at no less than 11.3’ msl during all hours.  This is effective from 0700 on 24 February until further notice.  This request is to provide necessary flows for chum egg incubation.

  - A teletype sent on 11 March requests BON forebay elevation be maintained at 71.5’ to 72.5’msl as a hard constraint, and 71.5’ to 72.0’ msl as a soft constraint from 0630 to 1700 on 02 and 03 April.  This request is to allow the Project to clean the latch pockets for the spill gate dogging mechanisms.

  - A teletype sent on 11 March replaces the teletype sent on 23 February (see 7.4).  It requests a gradual lowering of BON tailwater elevation:

    - Effective on 15 March at 0001, BON minimum tailwater elevation is 11.0’ msl.

    - Effective on 17 March at 0001, BON minimum tailwater elevation is 10.8’ msl.

    - Effective on 19 March at 0001, BON minimum tailwater elevation is 10.5’ msl.

    - Effective on 22 March at 0001, BON minimum tailwater limit is lifted.  The project will operate within its normal operating range.

  - A teletype sent on 12 March requests BON forebay return to normal operating range of 71.5’ to 76.5’ msl.  The teletype sent on 08 January (see 7.2) canceled as of 2400 on 14 March.

  - A teletype sent on 13 March outlines the operation of the B2CC.  The Project is authorized to open the B2CC once two kelts are observed on two consecutive days and a total of 20 kelts have been observed at the Juvenile Monitoring Facility.

    - If TDG exceeds 105% at Warrendale after 24 hours, the B2CC is to be operated and Spillbays 1 and 18 closed.

    - If TDG still exceeds 105% after 24 hours, the PH1 ITS is to be closed in addition.

    - If 105% TDG is still exceeded, then the B2CC is to be closed.

    - Once the B2CC is closed, PH1 will become the priority powerhouse, and PH1 ITS and Spillbays 1 and 18 will reopen.

  - While conducting fishway inspections, Project biologists observed 12 kelts on 10 March, four kelts on 11 March, and two kelts on 12 March in the vicinity of the B2CC bulkhead.

GLEN A. SMITH, P.E.

Operations Project Manager