### CENWP-OD-B																							22  March 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 12 of 2010, which covers the period from 14 through 20 March 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 112.7 to 120.4  kcfs.  Daily average project tailwater ranged from 10.6’  to 11.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.0’ msl.  Daily average river temperature ranged from 44 to 45ºF.  Secchi disk measurements ranged from 5.0’ to 6.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Units 1-10 were out of service 3 units at a time from March 14-20 to facilitate installation of trolley pipes by divers.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS valves were closed this reporting week.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 |  |  | STSs installed |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – Gatewell velocity testing.  Concluded on 18 March.

  - CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.

  - FFU- sea lion.  Observations continue.  Weekly reports of sea lion activities are now available. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- lamprey.  Cascades Island lamprey ramp camera remains installed.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  15 steelhead.  Please see http://www.fpc.org/adultsalmon/bonkeltcounts.htm for updated kelt counts.

  - Smith-Root- sea lion array.  Array remains installed in the UMT.  DIDSON installation to occur in early April.

  - WDFW- Fish Counting.  Video counting continues at WA shore and Bradford Island.

  - WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats continues.  Sea lion traps remain in position.  Trapping continues.

  - USDA Wildlife Services- Sea lion hazing.  Hazing from shore continues.

- FISHWAYS

  - Project biologists inspected 14-20 March.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 3/14-3/19 | ##### Avian line in spillway |  | ##### Moved by contractor | ##### Line was repositioned by contractor |  |
| 3/14-3/20 | ##### No attraction flow from spillbays 1 and 18 |  | ##### Excessive gas (TDG) levels | ##### Attraction flow to remain closed until gas levels can be controlled or April 1 gas waiver is initiated |  |
| PH1 ICE AND TRASH SLUICEWAY |  |  |  |  |  |
| 3/15-3/19 | ##### Sluiceway closed |  | ##### Trolley pipe install by divers | ##### Completion of installation |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| 3/16 | ##### Corner collector closed |  | ##### Excessive gas (TDG) levels | ##### Close sluiceway and attaction flow to lower gas. B2CC re-opened on 3/17 |  |
| WASHINGTON SHORE (WS) – nothing to report |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 3/14 | 42.3 | N/A |
| 3/15 | 42.7 | N/A |
| 3/16 | 43.0 | N/A |
| 3/17 | 43.4 | N/A |
| 3/18 | 43.6 | 44.5 |
| 3/19 | 43.7 | 44.4 |
| 3/20 | 43.8 | 44.9 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 17 March.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances.

  - Juvenile Fishways.

    - The B2 Corner Collector was opened 14 March but closed 16 March due to excessive total dissolved gas (TDG) readings downriver.  A regional agreement was reached to close the PH1 ice and trash sluiceway and the attraction flow from spillbays 1 and 18 in an attempt to lower TDG.  The corner collector was re-opened on 17 March.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains watered up.  It was closed from March 14-19th  for safety reasons as divers installed trolley pipes on the PH1 piernoses. It remained closed after trolley pipe installation in an attempt to lower TDG levels.

    - Hydrocannon remains in service.

    - TIES remain installed.

  - Lamprey Fishways.  All LPSs are dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal is complete.  Outfall removal has been postponed.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 08 January requests BON forebay maintain 71.5’ to 77.0’ msl as a soft constraint, and 71.5’ to 77.5’ msl as a hard constraint from 0001 on 09 January until 1800 on 31 March.  This is a modification of the 01 September teletype.  This request is to reduce the risk of flooding machinery and twisting bollards at BON locks, while still supporting spillwall construction at TDA.

  - A teletype sent on 08 September requests that BON operate the single highest priority unit at PH1 (currently Unit 1) as needed.  This is to reduce the risk of BON going outside the 1% efficiency range while supporting the high forebay request for TDA spillwall work.  This request is effective immediately until further notice.

  - A teletype sent on 23 February replaces the teletype sent on 30 December.  It requests BON tailwater elevation be maintained at no less than 11.3’ msl during all hours.  This is effective from 0700 on 24 February until further notice.  This request is to provide necessary flows for chum egg incubation.

  - A teletype sent on 11 March requests BON forebay elevation be maintained at 71.5’ to 72.5’msl as a hard constraint, and 71.5’ to 72.0’ msl as a soft constraint from 0630 to 1700 on 02 and 03 April.  This request is to allow the Project to clean the latch pockets for the spill gate dogging mechanisms.

  - A teletype sent on 11 March replaces the teletype sent on 23 February (see 7.4).  It requests a gradual lowering of BON tailwater elevation:

    - Effective on 15 March at 0001, BON minimum tailwater elevation is 11.0’ msl.

    - Effective on 17 March at 0001, BON minimum tailwater elevation is 10.8’ msl.

    - Effective on 19 March at 0001, BON minimum tailwater elevation is 10.5’ msl.

    - Effective on 22 March at 0001, BON minimum tailwater limit is lifted.  The project will operate within its normal operating range.

  - A teletype sent on 12 March requests BON forebay return to normal operating range of 71.5’ to 76.5’ msl.  The teletype sent on 08 January (see 7.2) canceled as of 2400 on 14 March.

  - A teletype sent on 13 March  requests that the corner collector be opened based on the triggers of observing two kelts per day for two consecutive days and a cumulative kelt number of 20 observed at Bonneville’s juvenile fish facility. Monitoring of gas levels at Warrendale will occur with contingencies in place for shutting down the Powerhouse 1 sluiceway and the spillway attraction flow if TDG levels are exceeded.

  - A teletype sent on 16 March requests BON to close the corner collector due to the exceedance of 105% TDG at the Warrendale fixed monitoring station.  The sluiceway should remain open but attraction flow from spillbays 1 and 18 should be closed.

  - A teletype sent on 17 March requests BON to open the corner collector and operate until further notice.  The sluiceway and attraction flow from spillbays 1 and 18 should be closed.

GLEN A. SMITH, P.E.

Operations Project Manager