### CENWP-OD-B																							05 April 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 14 of 2010, which covers the period from 28 March through 03 April 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 107.6 to 144.8 kcfs.  Daily average project tailwater ranged from 11.1’ to 14.7’ msl.  Daily average powerhouse forebay elevation ranged from 72.3’ to 75.8’ msl.  Daily average river temperature ranged from 46 to 47ºF.  Secchi disk measurements ranged from 4.5’ to 6.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 0.0 to 1.5 kcfs.

    - Spill bays 1 and 18 remained on sill most of the week due to excessive TDG in the river while the PH2 corner collector was in service (see 7.4-7.5).

    - The spillbays were closed on 02 April due to maintenance work in the spillway forebay (see 7.2).

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 3 was out of service from 0806 until 1421 on 01 April to repair lube oil fill line.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 3-9 was closed for cleaning from 1619 until 1622 on 01 April.

    - FV 5-9 and 6-9 were closed for cleaning from 1327 until 1347 on 29 March.

    - FV 6-9 was closed for cleaning from 1543 until 1605 on 01 April.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 3/29 | 781 | OK |
| 13 | 3/29 | 745 | OK |
| 14 | 3/29 | 788 | OK |
| 15 | 3/29 | 769 | OK |
| 16 | 3/29 | 714 | OK |
| 17 | 3/29 | 791 | OK |
| 18 | 3/29 | 786 | OK |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays continues.

  - CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.

  - FFU- sea lion.  Observations continue.  Weekly reports of sea lion activities are now available. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- lamprey.  Cascades Island lamprey ramp camera remains installed.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  32 steelhead.  Please see http://www.fpc.org/adultsalmon/bonkeltcounts.htm for updated kelt counts.

  - Smith-Root- sea lion array.  Array remains installed in the UMT.  DIDSON installation is scheduled to occur on 09 April.  Telemetry receivers were installed at three locations in the UMT on 02 April.

  - WDFW- Fish Counting.  Visual counting began at WA shore and Bradford Island on 01 April.

  - WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats continues.  Sea lion traps remain in position.  Trapping continues.

  - USDA Wildlife Services- Sea lion hazing.  Hazing from shore continues.

  - USDA Wildlife Services- Avian hazing.  Hazing from shore began on 01 April.

  - University of Idaho – lamprey. Collected 11 juvenile lamprey morts from the JMF.

- FISHWAYS

  - Project biologists inspected 28 March – 03 April

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 3/28-31 | ##### Spillbays 1 & 18 | ##### No attraction flow | ##### Excessive gas (TDG) levels | ##### Attraction flow to remain closed until gas levels can be controlled or April 1 gas waiver is initiated |  |
| 4/2 | ##### Spillbays 1 & 18 | ##### No attraction flow | ##### BON cleaning spill gate dog pockets | ##### Ops opened at 1714 on 4/2 (see 7.2). |  |
| 3/30 | ##### B-branch entrance | ##### Differential <1.0’ | ##### FV4-4/4-3 in manual | ##### Ops adjusted. |  |
| 4/3 | ##### B-branch entrance | ##### Differential >2.0’ | ##### FV4-4/4-3 in manual | ##### Ops adjusted. |  |
| 3/28, 4/3 | ##### A-branch weir | ##### Staff gage > 1.0’ | ##### Unknown | ##### No action. |  |
| PH1 ICE AND TRASH SLUICEWAY |  |  |  |  |  |
| 3/28-30 | ##### Sluiceway | ##### Closed | ##### Excessive gas (TDG) levels | ##### Sluiceway to remain closed until gas levels can be controlled or April 1 gas waiver is initiated |  |
| CASCADES ISLAND (CI)- nothing to report |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 3/28 | ##### Weir 38 | ##### Reading <1.0 | ##### Unknown | ##### Ops adjusted. |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 3/28 | 45.3 | 46.3 |
| 3/29 | 45.2 | 45.7 |
| 3/30 | 44.7 | 45.9 |
| 3/31 | 44.7 | 45.8 |
| 4/1 | 45.0 | 46.0 |
| 4/2 | 45.0 | 45.9 |
| 4/3 | 44.6 | 45.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 01 April.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 FOGs.  One gate remains out for maintenance, with a bulkhead installed.

    - Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances.

    - The AFF remains in bypass.

  - Juvenile Fishways.

    - The B2 Corner Collector was open from 25 March until 1607 on 29 March, and from 0723 on 30 March.  It remains open for the season (see 7.4- 7.5).  A regional agreement was reached to close the PH1 ice and trash sluiceway and the attraction flow from spillbays 1 and 18 in an attempt to lower TDG.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains watered up.  It was closed from 27 March until 1607 on 29 March, and from 0723 on 30 March until 0708 on 31 March.  It now remains open for the season (see 7.4-7.5).

    - Hydrocannon remains in service.

    - TIES remain installed.

  - Lamprey Fishways.  All LPSs are dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal is complete.  Outfall removal has been postponed.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Structural modifications scheduled to occur in late summer.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 11 March requests BON forebay elevation be maintained at 71.5’ to 72.5’msl as a hard constraint, and 71.5’ to 72.0’ msl as a soft constraint from 0630 to 1700 on 02 and 03 April.  This request is to allow the Project to clean the latch pockets for the spill gate dogging mechanisms.

  - A teletype sent on 25 March replaces the teletype sent on 24 March.  BON project is requested to continue operating with B2CC open, and spillbays 1 and 18 and the PH1sluiceway closed.

  - A teletype sent on 29 Monday requests BON close the B2CC on 29 March, or as soon as weather conditions allow, due to TDG exceedence.  The day after the B2CC is closed, reopen it at 0700 if the TDG reading at Warrendale is below 110%.  Do not operate the PH1 sluiceway and spillbays 1 and 18 when the B2CC is in operation.

  - A teletype sent on 31 March requests BON operate the B2CC, PH1 sluiceway, and spillbays 1 and 18, beginning at 0001 on 01 April and continuing until further notice.

GLEN A. SMITH, P.E.

Operations Project Manager