### CENWP-OD-B																							02 May 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 18 of 2010, which covers the period from 25 April through 01 May 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 170.5 to 195.6 kcfs.  Daily average project tailwater ranged from 15.5’ to 16.5’ msl.  Daily average powerhouse forebay elevation ranged from 75.3’ to 76.0’ msl.  Daily average river temperature ranged from 51 to 53ºF.  Secchi disk measurements ranged from 3.0’ to 5.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 99.2 to 99.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 was out of service from 0833 until 1155 on 26 April for gland water leak repair.

    - Unit 7 has remained out of service since 04 June 2007 for turbine rehab.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 13-17 was out of service from 0300 until 1052 on 27 April due to BGS repairs.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 1235 until 1245 on 26 April.

    - FV 3-7 was closed for cleaning from 1245 until 1255 on 26 April.

    - FV 5-9 and FV 6-9 were closed for cleaning from 1255 until 1310 on 26 April.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 4/28 | 659 | OK |
| 13 | 4/28 | 348 | OK |
| 14 | 4/28 | 379 | OK |
| 15 | 4/28 | 454 | OK, 15C VBS cleaned on 4/28 |
| 16 | 4/28 | 210 | OK |
| 17 | 4/28 | 416 | OK, VBSs cleaned on 4/28 |
| 18 | 4/28 | 659 | OK, VBSs cleaned on 4/28 |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays continues.

  - CRITFC- sea lion. Deployed hydrophones on 01 March in BON tailraces to track sea lion activity.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - FFU- sea lion.  Observations continue.  Weekly reports of sea lion activities are now available. If you would like to be included on the distribution list contact Robert Stansell-541-374-8801.

  - NOAA- lamprey.  Cascades Island lamprey ramp camera remains installed.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  56 steelhead, 14 salmon, and 7 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Two juvenile lamprey collected for University of Idaho researchers this week.

  - Smith-Root- sea lion array.  Array removal occurred on 28 April (See 4.5.6.).

  - WDFW- Fish Counting.  Visual counting continues.

  - WDFW, ODFW, CRITFC- Sea lion hazing/trapping.  Hazing from boats continues.  Sea lion traps remain in position.  Trapping continues.

  - USDA Wildlife Services- Sea lion hazing.  Hazing from shore continues.

  - USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

  - University of Idaho – lamprey.   Two juvenile lamprey collected from PSMFC SMP this reporting week.

  - University of Idaho - Adult salmon sampling continues for monitoring passage effects at the modified Cascades Island entrance.

- FISHWAYS

  - Project biologists inspected 25 April – 01 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| 4/27 | ##### BON | ##### Unit Priority | ##### BGS repair | ##### Corrected when repairs complete. |  |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 4/29-30 | ##### PH1 ice and trash sluiceway( ITS) | ##### Chain gate 10B < 2.5ft opening. | ##### In manual while program is worked on | ##### No action. |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |
| 4/28 | ##### UMT weir | ##### Reading <1.0’ | ##### Smith-Root array removal | ##### Corrected when removal complete. |  |
| 4/28 | ##### UMT channel | ##### North bulkhead installed | ##### Smith-Root array removal | ##### Corrected when removal complete. |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 4/27 | ##### B2CC | ##### Closed | ##### BGS repair | ##### Opened when repairs complete. |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 4/25 | 50.1 | 50.8 |
| 4/26 | 50.4 | 51.2 |
| 4/27 | 50.5 | 51.4 |
| 4/28 | 50.8 | 51.4 |
| 4/29 | 50.9 | 51.6 |
| 4/30 | 50.8 | 51.6 |
| 5/1 | 51.0 | 51.6 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 01 May.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 FOGs.  The repairs on one FOG have been completed.  Another FOG was removed for maintenance, with a bulkhead installed in its place.

    - Sea Lion Exclusion Devices (SLEDs) remain installed at all fishway entrances.

    - Sampling at the AFF continues.

    - The UMT bulkhead was installed at 1030 until 1345 on 28 April.   The Cascades Island ladder began going to orifice flow at approximately 1040, and was at orifice flow at approximately 1100 on 28 April.  The CI ladder was back in criteria at 1345.  This was necessary to support the removal of the Smith-Root array in the UMT.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.

    - Hydrocannon remains in service.

    - TIES are installed.

    - The B2CC was closed from 1333 on 26 April until 1052 on 27 April so repairs could be made to the boat exclusion device in the PH2 forebay (see 7.4 and 7.5).

  - Lamprey Fishways.  All LPSs are dewatered.

    - The Cascades Is. entrance weir remains installed.

    - The PH2 NDE ramp remains in the lowered position.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - PH1 Ice and Trash Sluiceway Wall Removal. Wall removal is complete.  Outfall removal has been postponed.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to occur in late summer.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.

  - A teletype sent on 26 April requests that Bonneville forebay be operated for the spring treaty fishery as follows:  0600 Tuesday, 27 April until 1800 Thursday, 29 April – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 26 April requests the B2 corner collector be closed immediately, until further notice due to a broken boat exclusion device in the PH2 forebay.  Limit PH2 flow to 50 KCFS (two main units, two fish units) while device is being repaired.  This operation was requested as a safety measure until repairs can be made.  Once repairs are made, operate as specified in the teletype sent on 09 April (see 7.2).

  - A teletype sent on 27 April requests BON operate as specified in teletype sent on 09 April (see 7.2).  Repairs to the boat exclusion device have been completed (see 7.4), and the B2 corner collector was reopened at 1045 on 27 April.

GLEN A. SMITH, P.E.

Operations Project Manager