### CENWP-OD-B																							27 June 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 26 of 2010, which covers the period from 20 through 26 June 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 281.4 to 345.5 kcfs.  Daily average project tailwater ranged from 22.3’ to 25.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.2’ msl.  Daily average river temperature ranged from 60 to 62ºF.  Secchi disk measurements ranged from 2.0’ to 3.2’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 99.5 to 163.9 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 2 was out of service from 0937 until 1658 on 21 June for thrust bearing cooler cleaning.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0927 until 1147 on 21 June for auto sync testing.

    - Unit 13 went out of service at 0733 on 14 June for four-year overhaul.

    - Unit 14 was out of service from 1035 until 1403 on 23 June for auto sync testing.

    - Unit 15 was out of service from 1352 until 1556 on 21 June for auto sync testing.

    - Unit 16 was out of service from 1411 until 1525 on 23 June for auto sync testing.

    - Unit 17 was out of service from 1535 until 1623 on 23 June for auto sync testing.

    - Unit 18 was out of service from 1113 until 1204 on 24 June for auto sync testing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was on standby to float debris from 0205-0413 on 24 June and 0208-0427 on 26 June,

    - F2 was on standby to float debris from 0404-0429 on 21 June and 0205-0431 on 25 June.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week. .

    - FV 3-9 was closed for cleaning from 1356 until 1411 on 24 June.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 29 June |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream have begun for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  36 steelhead, 29 salmon, and 37 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - WDFW- Fish Counting.  Visual counting continues.  Night counts began on 15 June.

  - USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

  - University of Idaho – lamprey.   No juvenile lamprey collected from PSMFC SMP this reporting week.  Radio and PIT tagging adult lamprey in the AFF.

  - University of Idaho - Adult salmon sampling continues for monitoring passage effects at the modified Cascades Island entrance.

- FISHWAYS

  - Project biologists inspected 20 - 26 June.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 6/22 | ##### PH1 SCC entrance | ##### Differential < 1.0’ | ##### Unknown | ##### Operators adjusted |  |
| 6/22 | ##### B-branch entrance | ##### Differential < 1.0’ | ##### System in manual | ##### Operators adjusted |  |
| 6/24 | ##### FV 3-7 trashrack | ##### Drawdown > 0.5’ | ##### Debris | ##### Riggers cleaned |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |
| 6/26 | ##### FV5-9 trashrack | ##### Drawdown > 0.5’ | ##### Debris | ##### Riggers cleaned |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 6/20-21 | ##### PH2 entrance gates | ##### Submerged <13’ | ##### In manual | ##### Operators adjusted |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - Design of a mechanical velocity meter at the PH2 south monolith is in progress.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 6/20 | 57.5 | 58.4 |
| 6/21 | 57.7 | 58.6 |
| 6/22 | 57.9 | 58.8 |
| 6/23 | 58.4 | 59.3 |
| 6/24 | 58.9 | 59.7 |
| 6/25 | 59.4 | 60.2 |
| 6/26 | 59.6 | 60.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 25 June.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sea Lion Exclusion Devices (SLEDs) were removed from WA shore and PH1 fishway entrances on 21 June and from B-branch entrance on 22 June.  The Cascades Island SLED remains in place until a crane can be rented.

    - Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.

    - WA shore, Cascades Is., and Bradford Is. ladder remain in shad passage mode.

    - Operators began maintaining 0.5’ of head at the PH2 fishway entrances on 15 June for lamprey passage during night hours.  Table Bon-5 of the FPP is being utilized as a guideline.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chaingates 1A and 1B were adjusted to 71’ and 73’ msl, respectively, on 14 June.  The automated gates remain in manual until changes to the operating program are made.

    - Hydrocannon remains in service.

    - TIES remain installed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  Cascade Is. LPS remains in service. Scheduled to operate Sunday night through Friday.

    - The PH2 NDE ramp remains in the lowered position. It was shut down on 04 June due to high tailwater. Normally scheduled to operate Sunday night through Friday.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to begin on 06 July.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.

  - A teletype sent on 11 June requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Wednesday, 16 June until 1800 Friday, 18 June and 0600 Tuesday, 22 June until 1800 Thursday, 24 June – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 15 June requests BON project begin the summer spill test at 0430 on 16 June until 0430 on 20 July.  If flows are too high, BON is requested to spill at an even rate until it is possible to begin the test.  Two treatments will be used in a block test: 85kcfs day/121 kcfs night and 95 kcfs for 24 hours.

  - A teletype sent on 16 June requests Bonneville operate PH2 units within 5 MW of the mid to lower end of the 1% efficiency range (approx. 14 kcfs or less), hard constraint, effective immediately.  This operation was requested to reduce high levels of fish descaling observed at the Juvenile Monitoring Facility.

  - A teletype sent on 22 June cancels the teletype sent on 16 June (see 7.5).  Bonneville PH2 units can now operate within the standard 1% range.  Verbal notification was given to the project to resume normal operations on 21 June.

  - A teletype sent on 22 June reinitiates the 16 June teletype (see 7.5).  Effectively immediately, it is requested that Bonneville operate PH2 units within 5 MW of the mid to lower end of the 1% efficiency range (approx. 14 kcfs or less), hard constraint.  This operation was requested to reduce high levels of fish descaling observed at the Juvenile Monitoring Facility.

  - A teletype sent on 25 June requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Tuesday, 29 June until 1800 Thursday, 01 July – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

GLEN A. SMITH, P.E.

Operations Project Manager