### CENWP-OD-B																							05 July 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 27 of 2010, which covers the period from 27 June through 03 July 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 244.5 to 324.5 kcfs.  Daily average project tailwater ranged from 19.7’ to 24.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.2’ to 74.7’ msl.  Daily average river temperature ranged from 62 to 63ºF.  Secchi disk measurements ranged from 3.5’ to 5.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 90.2 to 142.8 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 4 was out of service from 0305 on 28 June until 2106 on 29 June for annual maintenance.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 13 went out of service at 0733 on 14 June for four-year overhaul.

    - Unit 15 was out of service from 1011 until 1153 on 30 June for STS replacement.

    - Unit 17 was out of service from 0802 until 1211 on 01 July for strainer repair.

    - Unit 18 was out of service from 0114 until 0955 on 27 June due to STS failure.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 3-9 was closed for cleaning from 0956 until 1022 on 28 June and from 1617 until 1628 on 01 July.

    - FV 5-9 was closed for cleaning from 1329 until 1340 on 01 July.

    - FV 6-9 was closed for cleaning from 1329 until 1340 on 01 July.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 6/29 | 679 | OK |
| 13 | 6/29 | 306 | OK |
| 14 | 6/29 | 679 | OK |
| 15 | 6/29 | 679 | OK |
| 16 | 6/29 | 559 | OK |
| 17 | 6/29 | 680 | OK |
| 18 | 6/29 | 669 | OK |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream continue for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  8 steelhead, 152 salmon, and 78 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - WDFW- Fish Counting.  Visual counting continues.  Night counts began on 15 June.

  - USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

  - University of Idaho – lamprey.   Radio and PIT tagging adult lamprey in the AFF.

  - University of Idaho - Adult salmon sampling concluded on 30 June.

- FISHWAYS

  - Project biologists inspected 27 June – 03 July

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 6/30, 7/2-3 | ##### PH1 SCC entrance | ##### Differential < 1.0’ | ##### Unknown | ##### Operators adjusted |  |
| 6/29 | ##### B-branch entrance | ##### Differential > 2.0’ | ##### System in manual | ##### Operators adjusted |  |
| CASCADES ISLAND (CI) Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 6/29, 7/1 | ##### PH2 entrance gates | ##### Submerged <13’ | ##### In manual | ##### Operators adjusted |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

    - Temperatures are unavailable this week but are expected to return next week.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 6/27 | N/A | N/A |
| 6/28 | N/A | N/A |
| 6/29 | N/A | N/A |
| 6/30 | N/A | N/A |
| 7/1 | N/A | N/A |
| 7/2 | N/A | N/A |
| 7/3 | N/A | N/A |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 02 July.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - The Cascades Island SLED was removed on 30 June, and the slot filler was installed in its place. All other SLEDs were previously removed for the season.

    - Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.

    - WA shore, Cascades Is., and Bradford Is. ladder remain in shad passage mode.

    - Operators continue to maintain 0.5’ of head at the PH2 fishway entrances for lamprey passage during night hours.  Table Bon-5 of the FPP is being utilized as a guideline.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chaingates 1A and 1B remain set to 71’ and 73’ msl, respectively.  The automated gates are now operating in auto.

    - Hydrocannon remains in service.

    - TIES remain installed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  Cascade Is. LPS remains in service. Scheduled to operate Sunday night through Friday.  The CI SLED was removed on 30 June, and the slot filler was installed in its place.

    - The PH2 NDE ramp remains in the lowered position. Scheduled to operate Sunday night through Friday.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to begin on 06 July.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 09 April requests spill for juvenile fish passage begin at 0001 hours on Saturday, 10 April and continue until further notice. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2010 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30 kcfs, then operate to minimum discharge and spill to pass inflow.

  - A teletype sent on 15 June requests BON project begin the summer spill test at 0430 on 16 June until 0430 on 20 July.  If flows are too high, BON is requested to spill at an even rate until it is possible to begin the test.  Two treatments will be used in a block test: 85kcfs day/121 kcfs night and 95 kcfs for 24 hours.

  - A teletype sent on 22 June requests Bonneville operate PH2 units within 5 MW of the mid to lower end of the 1% efficiency range (approx. 14 kcfs or less), hard constraint, effective immediately.  This operation was requested to reduce high levels of fish descaling observed at the Juvenile Monitoring Facility.  This operation originally began on 16 June.

  - A teletype sent on 25 June requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Tuesday, 29 June until 1800 Thursday, 01 July – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 28 June requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Tuesday, 06 July until 1800 Thursday, 08 July – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 29 June requests Bonneville forebay be operated from 1000-1800 each day on 9-11 July as follows: maintain 73.0-74.0’ msl, soft constraint.  This operation was requested to support a kite board event at the Port of Hood River.

  - A teletype sent on 01 July requests Bonneville forebay be operated from 2000-2300 on 04 July as follows: 75.8-76.5’ msl, hard constraint, 76.0-76.5’ msl, soft constraint.  This operation was requested to support the Hood River 4th of July fireworks show. At all other times from 03 – 05 July during daylight hours, it is requested Bonneville maintain a lower pool to benefit recreational users.

  - A teletype sent on 02 July requests BON project begin the summer spill test effective immediately until 0430 on 20 July.  Two treatments will be used in a block test: 85kcfs day/121 kcfs night and 95 kcfs for 24 hours.  The teletype also requests a continuation of the current PH2 operation (see 7.4) until Tuesday 06 July at 0900.

  - A teletype sent on 02 July requests BON Project close the PH2 corner collector (B2CC) on Wednesday 07 July from 0700-1100.  If the B2CC is not closed on Wednesday, the project can make another attempt to close it on 08 July from 0700-1100.  Operate MU 15 at the low end of the 1% efficiency range.  This operation is to support the repair of PH2 forebay transducers.

GLEN A. SMITH, P.E.

Operations Project Manager