### CENWP-OD-B																							26 July 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 30 of 2010, which covers the period from 18 through 24 July 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 140.3 to 179.4 kcfs.  Daily average project tailwater ranged from 12.7’ to 15.1’ msl.  Daily average powerhouse forebay elevation ranged from 74.3’ to 75.8’ msl.  Daily average river temperature ranged from 67 to 69ºF.  Secchi disk measurements ranged from 4.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 82.9 to 99.9 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 10 was out of service from 2100 on 18 July until 1558 on 21 July for annual maintenance.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0041 on 19 July until 1532 on 21 July for T-11 biannual maintenance.

    - Unit 13 went out of service at 0733 on 14 June for four-year overhaul.

    - Unit 14 was out of service from 0041 on 19 July until 1538 on 21 July for T-11 biannual maintenance.

    - Unit 18 was out of service from 0249 until 0707 on 22 July due to high temperature alarms.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F2 was out of service from 2201 on 23 July until 0857 on 24 July.  The unit had been shut off for nighttime lamprey operations, but operators were unable to place the unit back in service by 0430 due to a loose timer wire.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV1-1 was closed for cleaning from 0735 until 0830 on 19 July.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 26 July. |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Hydrophone installation in PH1, PH2, and spillway forebays complete. Tagged fish releases upstream continue for dam passage and survival evaluations. Sort by Code operations at the SMF continued this week to evaluate acoustic tagging effects on juvenile salmonids.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week:  4 steelhead, 13 salmon, and 4 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - WDFW- Fish Counting.  Visual counting continues.  Night counts continue.

  - USDA Wildlife Services- Avian hazing.  Hazing from shore continues.

  - University of Idaho – lamprey.   Radio and PIT tagging adult lamprey in the AFF.

- FISHWAYS

  - Project biologists inspected 18-24 July.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 7/18-19 | ##### Chain gate 6C | ##### Submerged < 2.0’ | ##### Slack cable trouble | ##### See 4.6.5 | ##### 10-184724 |
| 7/22,24 | ##### PH1 ITS chaingates | ##### Incorrect position | ##### PLC error | ##### Operators reset |  |
| CASCADES ISLAND (CI) Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 7/18-22 | ##### PH2 entrance gates | ##### Submerged <13’ | ##### In manual | ##### Operators adjusted |  |
| 7/24 | ##### PH2 entrances | ##### Reading < 1.0’ | ##### F2 OOS | ##### See 1.4.1. Electricians repaired |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average | AFF average | SMF average |
| --- | --- | --- | --- | --- |
| 7/18 | 66.1 | 66.1 | 66.0 | 66.2 |
| 7/19 | 66.0 | 66.0 | 65.9 | 66.1 |
| 7/20 | 66.2 | 66.1 | 66.1 | 66.2 |
| 7/21 | 66.4 | 66.4 | 66.3 | 66.4 |
| 7/22 | 66.9 | 66.7 | 66.7 | 66.9 |
| 7/23 | 67.7 | 67.4 | 67.5 | 67.6 |
| 7/24 | 68.4 | 68.5 | 68.2 | 68.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 23 July.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sampling at the AFF continues.  The downstream exit bulkhead remained in the lowered position after sampling this week to keep the ladder in criteria and shad off the weir 37 bleed off valve.  The automatic blow down function for the weir 37 bleed off valve was programmed on 19 May to operate every six hours.

    - Operators continue to maintain 0.5’ of head at the PH2 fishway entrances for lamprey passage during night hours.  Table Bon-5 of the FPP is being utilized as a guideline.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.

    - Hydrocannon remains in service.

    - TIES remain installed.

  - PH1 ITS Chain gate 6C was stuck at elevation 72.8’ msl due to slack cable troubles and unable to move in manual. If forebay elevations are below 74.8’ the gate experienced <2.0’ opening, and will be out of criteria.   The gate was repaired on 19 July.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains in service. Scheduled to operate Sunday night through Friday.

    - The PH2 NDE ramp remains in the lowered position and in service.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to begin in July.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 02 July requests BON project begin the summer spill test effective immediately until 0430 on 20 July.  Two treatments will be used in a block test: 85kcfs day/121 kcfs night and 95 kcfs for 24 hours.

  - A teletype sent on 09 July requests Bonneville forebay be operated from 1200-1800 each day on 16-18 July as follows: maintain 73.0-74.0’ msl, soft constraint.  This operation was requested to support a kite board event at the Port of Hood River.

  - A teletype sent on 16 July modifies the teletype sent on 02 July (see 7.2).  It requests BON project to continue the summer spill test until 0430 on 21 July.  Two treatments will be used in a block test: 85kcfs day/121 kcfs night and 95 kcfs for 24 hours.

  - A teletype sent on 16 July requests BON project begin the summer spill at 0430 on 21 July until 2400 on 31 August.  Spill 75kcfs during the day and gas cap at night.  Day time hours are defined in table BON-5 of the 2010 FPP.  Spill in accordance with pattern in table BON-16 of the 2010 FPP.  If flows are insufficient, the project is requested to reduce to minimum generation at night and spill the remainder.  The minimum generation requirement is 30 kcfs, and the minimum spill level is 50 kcfs

  - A teletype sent on 16 July requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Tuesday, 20 July until 1800 Thursday, 22 July – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 23 July requests that Bonneville forebay be operated for the treaty fishery as follows:  0600 Tuesday, 27 July until 1800 Thursday, 29 July – operate within 1.5’ band, hard constraint.  This is to limit pool fluctuation and reduce wear and tear on equipment.

GLEN A. SMITH, P.E.

Operations Project Manager