### CENWP-OD-B																							30 August 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 35 of 2010, which covers the period from 22 through 28 August 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 111.0 to 118.3 kcfs.  Daily average project tailwater ranged from 10.2’ to 10.5’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 76.0’ msl.  Daily average river temperature ranged from 69 to 71ºF.  Secchi disk measurements averaged 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 68.1 to 74.7 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 went out of service at 0841 on 02 August for five year overhaul.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 13 was out of service at 0733 on 14 June until 0905 on 24 August for four-year overhaul.

    - Unit 18 was out of service from 0054 on 24 August until 2007 on 25 August for annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 1104 until 1121 on 26 August.

    - FV 3-9 was closed for cleaning from 1045 until 1050 on 26 August.

    - FV 5-9 was closed for cleaning from 0915 until 0930 on 26 August.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 8/23 | 691 | OK |
| 13 | 8/23 | 69 | OK |
| 14 | 8/23 | 104 | OK |
| 15 | 8/23 | 220 | OK |
| 16 | 8/23 | 32 | OK |
| 17 | 8/23 | 128 | OK |
| 18 | 8/23 | 689 | OK |

  - Dewatering and Fish Salvage.  No dewatering/fish salvage activities occurred this week.

- RESEARCH

  - Battelle – survival study.  Monitoring acoustic tagged fish passage concluded on 12 August.

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.  Sampling protocols returned to normal on 24 August due to water temperatures <70.0 °F.  See Appendix G in the 2010 FPP for details.

  - NOAA- lamprey.  PIT tagging adult lamprey in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  No fallbacks recorded crossing the separator bars for this reporting week.  Gas Bubble Trauma (GBT) examinations occur two days per week at the JMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  Modified sampling protocols were implemented from 06-23 August due to water temperatures >70.0’.  See Appendix J in the 2010 FPP for details.  Truck releases from McNary Dam, Lower Granite, Little Goose, and Lower Monumental dams continue.

  - WDFW- Fish Counting.  Visual counting continues.  Night counts continue.

  - WDFW- Tule counting.  Tule counting continues.

  - University of Idaho – lamprey.   Radio and PIT tagging adult lamprey in the AFF.

- FISHWAYS

  - Project biologists inspected 22-28 August.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) Nothing to report. |  |  |  |  |  |
| CASCADES ISLAND (CI) Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) Nothing to report. |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average | AFF average | SMF average |
| --- | --- | --- | --- | --- |
| 8/22 | 68.5 | 69.0 | 68.5 | 69.0 |
| 8/23 | 68.2 | 68.4 | 68.2 | 68.6 |
| 8/24 | 68.3 | 68.5 | 68.3 | 68.7 |
| 8/25 | 69.0 | 69.1 | 68.9 | 69.4 |
| 8/26 | 69.2 | 69.2 | 69.2 | 69.7 |
| 8/27 | 68.9 | 69.1 | 68.8 | 69.3 |
| 8/28 | 68.9 | 69.1 | 68.8 | 69.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 27 August.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sampling at the AFF continues. Normal sampling protocols resumed on 24 August due to daily average water temperatures <69.5 °F.  See Appendix G in the 2010 FPP for details. http://www.nwd-wc.usace.army.mil/tmt/documents/fpp/2010/changes/APPG_TRAP_Revised_20100519.pdf

    - Operators continue to maintain 0.5’ of head at the PH2 fishway entrances for lamprey passage during night hours.  Table Bon-5 of the FPP is being utilized as a guideline.  This operation is scheduled to conclude on 31 August.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened at 0740 on 04 August as outlined in the teletype sent on 29 July (See 7.3).  Chain gate 7A is set to 72’ msl.

    - Hydrocannon remains in service.

    - TIES remain installed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains in service. Scheduled to operate Sunday night through Friday.

    - The PH2 NDE ramp remains in the lowered position and in service

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to resume when fish counts drop below 1,000.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 16 July requests BON project begin the summer spill at 0430 on 21 July until 2400 on 31 August.  Spill 75kcfs during the day and gas cap at night.  Day time hours are defined in table BON-5 of the 2010 FPP.  Spill in accordance with pattern in table BON-16 of the 2010 FPP.  If flows are insufficient, the project is requested to reduce to minimum generation at night and spill the remainder.  The minimum generation requirement is 30 kcfs, and the minimum spill level is 50 kcfs

  - A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.

  - A teletype sent on 18 August requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 24 August until 1800 Friday, 27 August;   0600 Tuesday, 30 August until 1800 Friday, 03 September; and 0600 Tuesday, 07 September until 1800 Friday, 10 September.  This is to limit pool fluctuation and reduce wear and tear on equipment.

GLEN A. SMITH, P.E.

Operations Project Manager