### CENWP-OD-B																						20 September 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 38 of 2010, which covers the period from 12 through 18 September 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 72.7 to 104.6 kcfs.  Daily average project tailwater ranged from 7.4’ to 9.3’ msl.  Daily average powerhouse forebay elevation ranged from 75.4’ to 76.1’ msl.  Daily average river temperature ranged from 66 to 67ºF.  Secchi disk measurements averaged 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.4 to 1.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 has remained out of service since 02 August for five year overhaul.

    - Unit 1 had a 1% violation on 17 September due to model verification testing.  Unit 1 went out of service at 1309 on 17 September due to sticking wicket gates.

    - Unit 2 had a 1% violation on 16 and 17 September due to model verification testing.

    - Unit 3 had a 1% violation on 16 September due to model verification testing.

    - Unit 4 had a 1% violation on 15 and 16 September due to model verification testing.

    - Unit 5 had a 1% violation on 15 September due to model verification testing.

    - Unit 6 had a 1% violation on 15 September due to model verification testing.

    - Unit 7 was out of service from 1542 until 1610 on 16 September due to exciter trouble.  1% violation on 14 September due to model verification testing.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 8 had a 1% violation on 14 September due to model verification testing.

    - Unit 10 was out of service from 1553 on 13 September until 1334 on 14 September due to a transformer work trip.  1% violation on 14 and 17 September due to bank 9/10 testing and model verification testing.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 went out of service at 0724 on 13 September for four year overhaul.

    - Unit 15 was out of service from 1255 on 12 September until 1036 on 14 September for annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 1540 until 1600 on 13 September.

    - FV 3-7 was closed for cleaning from 1600 until 1615 on 13 September.

    - FV 3-9 was closed for cleaning from 1600 until 1615 on 13 September and from 1509 until 1513 on 14 September.

    - FV 5-9 was closed for cleaning from 1520 until 1540 on 13 September.

    - FV 6-9 was closed for cleaning from 1500 until 1520 on 13 September and from 1025 until 1030 on 17 September.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | N/A | N/A | Inspection scheduled for week of 20 September |

  - Dewatering and Fish Salvage. The following dewatering and fish salvage activities occurred this week:

    - Biologists recovered 75 juvenile shad from Unit 12 gatewell on 13 September.  All were released in good condition.  Unit 12 is OOS for four year overhaul.

    - Biologists recovered one bluegill, one perch, 50 crawdads, and 20 sculpin from Unit 9 tail logs on 16 September.  All were released in good condition.

    - Biologists recovered 50 sturgeon from Unit 12 draft tube at 1300 on 14 September. All released in good condition at the downstream boat ramp.  Unit 12 is OOS for four year overhaul.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week: four salmon.  Truck releases from McNary Dam, Lower Granite, Little Goose, and Lower Monumental dams continue.

  - University of Idaho – steelhead sampling.  Worked with CRITFC to collect steelhead blood samples from the AFF on 22 and 23 September to look at adult steelhead physiology.

  - WDFW- Fish Counting.  Visual counting continues.  Night counts continue.

  - WDFW- Tule counting.  Tule counting continues.

- FISHWAYS

  - Project biologists inspected 12 through 18 September.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |  | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |  |
| 9/12-13 | ##### PH1 SCC | ##### Differential <1.0’ | ##### Unknown | ##### Operators adjusted. |  |  |  |
| 9/17-18 | ##### BI fish exit | ##### Needs cleaning | ##### Aquatic vegetation | ##### Riggers cleaned |  |  |  |
| 9/17 | ##### BI weir | ##### Reading > 1.0’ | ##### Unknown | ##### Operators adjusted. |  |  |  |
| 9/17 | ##### A-branch weir | ##### Reading > 1.0’ | ##### Unknown | ##### Operators adjusted. |  |  |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |  |  |
| 9/14 | Weir 37 staff gauge | Reading <1.0’ | Unknown |  | Operators adjusted. |  |  |
| WASHINGTON SHORE (WS) - Nothing to report. |  |  |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average | AFF average | SMF average |
| --- | --- | --- | --- | --- |
| 9/12 | 65.1 | 65.5 | 65.0 | 65.6 |
| 9/13 | 65.5 | 65.7 | 65.4 | 65.9 |
| 9/14 | 65.6 | 65.9 | 65.6 | 66.1 |
| 9/15 | 65.6 | 65.9 | 65.6 | 66.1 |
| 9/16 | 65.7 | 66.0 | 65.7 | 66.2 |
| 9/17 | 65.9 | 66.2 | 65.9 | 66.4 |
| 9/18 | 66.1 | 66.3 | 66.1 | 66.6 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 18 September.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sampling at the AFF continues.

    - The Bradford Island fish exit was closed for cleaning from 1600 until 1615 on 13 September, from 1509 until 1513 on 14 September, and from 1007 until 1015 on 17 September.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - B2CC remains closed for the season.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened at 0740 on 04 August as outlined in the teletype sent on 29 July (See 7.2).  Chain gate 7A is set to 72’ msl.

    - Hydrocannon remains in service.

    - TIES remain installed.  They are scheduled for removal the week of 19 September.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS operations concluded on 11 September.

    - The PH2 NDE ramp remains in the lowered position and is not currently used.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is in progress.  Shoring of the walls is scheduled to resume when fish counts drop below 1,000.

  - PH1 juvenile outfall removal.  Removal work above water line is scheduled to occur mid-October.  In-water work is scheduled to occur between 1-10 November.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.

  - A teletype sent on 09 September requests BON forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows: 0600 Monday, 13 September until 1800 Friday, 17 September.  This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 17 September requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 21 September until 1800 Friday, 24 September.   This is to limit pool fluctuation and reduce wear and tear on equipment.

GLEN A. SMITH, P.E.

Operations Project Manager