### CENWP-OD-B																						27 September 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 39 of 2010, which covers the period from 19 through 25 September 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 77.2 to 95.8 kcfs.  Daily average project tailwater ranged from 7.7’ to 9.2’ msl.  Daily average powerhouse forebay elevation ranged from 75.1’ to 76.0’ msl.  Daily average river temperature ranged from 66 to 67ºF.  Secchi disk measurements averaged 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.

    - Bay 1 was on sill from 1020 until 1121 on 21 September for the stilling basin survey.

    - Bay 18 was on sill from 1136 until 1251 on 21 September for the stilling basin survey.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 has remained out of service since 02 August for five year overhaul.

    - Unit 1 has remained out of service since 17 September due to sticking wicket gates.  Unit 1 had a 1% violation on 20 September due to wicket gate testing.

    - Unit 9 has remained out of service since 04 August 2008 for turbine rehab.

    - Unit 10 went out of service at 0030 on 21 September due to Bank 9/10 outage for Unit 9 reconnect.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 has remained out of service since 13 September for four year overhaul.

    - Unit 13 was out of service from 0244 until 1307 on 21 September, and from 0938 until 1111 on 22 September for air gap sensor testing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 1021 until 1040 on 23 September.

    - FV 3-7 was closed for cleaning from 0842 until 0900 on 24 September.

    - FV 3-9 was closed for cleaning from 1349 until 1356 on 21 September and from 0842 until 0900 on 24 September.

  - STS/VBS inspections.  The following STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 9/20 | 480 | OK |
| 13 | 9/20 | 208 | OK |
| 14 | 9/20 | 369 | OK |
| 15 | 9/20 | 456 | OK |
| 16 | 9/20 | 31 | OK |
| 17 | 9/20 | 480 | OK |
| 18 | 9/20 | 533 | OK |

  - Dewatering and Fish Salvage. No dewatering and fish salvage activities occurred this week.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars for this reporting week: nine salmon and two unknown salmonids.  Truck releases from McNary Dam, Lower Granite, Little Goose, and Lower Monumental dams continue.

  - University of Idaho – steelhead sampling.  Worked with CRITFC to collect steelhead blood samples from the AFF on 22 and 23 September to examine adult steelhead physiology.

  - WDFW- Fish Counting.  Visual counting continues.  Nighttime counts are scheduled to conclude on 30 September.

  - WDFW- Tule counting.  Tule counting continues.

- FISHWAYS

  - Project biologists inspected 19 through 25 September.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |
| 9/20, 23 | ##### PH1 SCC | ##### Differential <1.0’ | ##### Unknown | ##### Operators adjusted. |  |  |
| 9/20-24 | ##### BI fish exit | ##### Needs cleaning | ##### Aquatic vegetation | ##### Riggers cleaned on 21, 23, and 24 September. |  |  |
| 9/20 | ##### BI weir | ##### Reading > 1.0’ | ##### Unknown | ##### Operators adjusted. |  |  |
| 9/20-21 | ##### FV3-9 picket leads | ##### Drawdown > 0.3’ | ##### Aquatic vegetation | ##### Riggers cleaned. |  |  |
| 9/22 | ##### A-branch, B-branch and BI weirs | ##### Reading <1.0’ | ##### FV3-7 and FV3-9 briefly closed to support forebay survey | ##### Returned to normal operation |  |  |
| 9/23 | ##### A-branch weir | ##### Reading >1.0’ | ##### Unknown | ##### No action taken. |  |  |
| 9/24 | ##### FG 3-3 | ##### Incorrect position | ##### Unknown | ##### Operators adjusted. |  |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |  |
| WASHINGTON SHORE (WS) - Nothing to report. |  |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average | AFF average | SMF average |
| --- | --- | --- | --- | --- |
| 9/19 | 66.3 | 66.5 | 66.2 | 66.8 |
| 9/20 | 66.0 | 66.3 | 66.0 | 66.5 |
| 9/21 | 65.6 | 65.8 | 65.6 | 66.1 |
| 9/22 | 65.4 | 65.7 | 65.3 | 65.9 |
| 9/23 | 65.1 | 65.4 | 65.1 | 65.6 |
| 9/24 | 64.8 | 65.1 | 64.9 | 65.4 |
| 9/25 | 64.8 | 65.1 | 64.8 | 65.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 24 September.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sampling at the AFF continues.

    - The Bradford Island fish exit was closed for cleaning from 1349 until 1356 on 21 September, from 1006 until 1020 on 23 September, and from 0842 until 0900 on 24 September.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - B2CC remains closed for the season.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened at 0740 on 04 August as outlined in the teletype sent on 29 July (See 7.2).  Chain gate 7A is set to 72’ msl.

    - The PH1 ITS was closed from 0722 until 1445 on 22 September due to survey work in the PH1 forebay.

    - Hydrocannon remains in service.

    - Four TIES remain installed.  One TIE was removed on 22 September, and one was removed on 23 September.  The remaining TIES are scheduled for removal the week of 26 September.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS operations concluded on 11 September.

    - The PH2 NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls within 50’ of the Cascades Island fishway is scheduled to resume when fish counts drop below 1,000.

  - PH1 juvenile outfall removal.  Removal work above water line is scheduled to occur mid-October.  In-water work is scheduled to occur between 1-10 November.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 29 July requests BON project change PH1 unit priority as follows: 1, 3,7,6,2,4,5,8,10,9, effective immediately until further notice.  This moves Unit 7 to third in priority.  This operation is necessary to complete a 100 day operation per PH1 rehab contract.  The project is requested to close automatic chain gate 6C and open manual gate 7A to minimize impacts to fish passage.

  - A teletype sent on 17 September requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 21 September until 1800 Friday, 24 September.   This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 20 September cancels the teletype sent on 17 September (see 7.3).

  - A teletype sent on 24 September requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Monday, 27 September until 1800 Wednesday, 29 September.   This is to limit pool fluctuation and reduce wear and tear on equipment.

  - Bonneville Fisheries sent out the following Memorandum’s for the Record:

    - 100915: Steelhead mortality on PIT detector walkway grating at Bradford Island fish ladder.

    - 100921: Chinook mortality in the AFF, severe marine mammal injury.

    - 100923: Two chinook mortalities, found on the Valve 15 trashrack.  One fish had been sampled by CRITFC on 21 September and appeared to recover from anesthesia.

GLEN A. SMITH, P.E.

Operations Project Manager