### CENWP-OD-B																						24 October 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2010, which covers the period from 17 through 23 October 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 85.0 to 112.5 kcfs.  Daily average project tailwater ranged from 8.4’ to 9.9’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.4’ msl.  Daily average river temperature ranged from 63 to 65ºF.  Secchi disk measurements averaged 7.0’ all week.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.2 to 1.3 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 0 returned to service at 1038 on 19 October.  It had been out of service since 02 August for five year overhaul.

    - Unit 1 has remained out of service since 17 September due to sticking wicket gates.

    - Unit 2 has remained out of service since 05 October for five year overhaul.

    - Unit 4 was out of service from 0932 on 18 October until 1515 on 21 October due to BPA 230kV transmission MW restriction.

    - Unit 7 was out of service from 1500 on 19 October until 1344 on 21 October for 100 day inspection.

    - Unit 8 was out of service from 0954 on 18 October until 1500 on 19 October and from 1344 until 1515 on 21 October due to BPA 230kV transmission MW restriction.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 has remained out of service since 13 September for four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 1104 until 1114 on 21 October.

    - FV 3-9 was closed for cleaning from 1148 until 1155 on 21 October.

    - FV 5-9 was closed for cleaning from 1135 until 1142 on 21 October.

    - FV 6-9 was closed for cleaning from 1123 until 1131 on 21 October.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week:

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | NA | OOS | U12 is out of service. |
| 13 | 10/19 | 686 | OK |
| 14 | 10/19 | 677 | OK |
| 15 | 10/19 | 699 | OK |
| 16 | 10/19 | 569 | OK |
| 17 | 10/19 | 698 | OK |
| 18 | 10/19 | 698 | OK |

  - Dewatering and Fish Salvage. No fish salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC - Annual chinook, coho, sockeye and steelhead sampling in the AFF concluded on 21 October.

  - PSMFC- smolt monitoring.  Juvenile fish condition and index monitoring continues. Sampling is scheduled to conclude on 31 October.  Fallbacks recorded crossing the separator bars for this reporting week: 12 salmon, three unknown salmonids, and two steelhead.  Truck releases from Lower Granite, Little Goose, and Lower Monumental dams continue.

  - WDFW- Fish Counting.  Visual counting continues. Visual counting is scheduled to conclude on 31 October.

- FISHWAYS

  - Project biologists inspected 17 through 23 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) – Nothing to report. |  |  |  |  |  |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |  |
| 10/20 | ##### PH2 entrances | ##### Differential <1.0’ | ##### Unknown | ##### Operators adjusted |  |  |
| All week | ##### Weir 38 | ##### Reading <1.0’ | ##### Unknown | ##### No action taken. |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 10/17 | 60.9 | 61.4 |
| 10/18 | 60.6 | 61.0 |
| 10/19 | 60.4 | 60.7 |
| 10/20 | 59.9 | 60.3 |
| 10/21 | 59.9 | 60.3 |
| 10/22 | 60.0 | 60.3 |
| 10/23 | 59.9 | 60.3 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 23 October.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Sea lion exclusion bars remain in 11 of 12 floating orifice gates (FOGs).  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - Sampling at the AFF concluded on 21 October.  The AFF is scheduled to be dewatered the week of 24 October.

    - The Bradford Island fish exit was closed for cleaning from 1137 until 1148 on 21 October.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - B2CC remains closed for the season.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened on 04 August.  Chain gate 7A is set to 72’ msl.

    - The Hydrocannon remains in service.

    - All TIEs have been removed.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.

    - The PH2 NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain in service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in FY11.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls within 50’ of the Cascades Island fishway is scheduled to resume when fish counts drop below 1,000.

  - PH1 juvenile outfall removal.  Removal work above water line began on 11 October.  In-water work is scheduled to occur between 1-10 November.

  - BGS removal. Scheduled to begin mid-December.

  - NDE lamprey modifications. Contractor will begin mobilizing on 15 November.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1, 10, 9, 3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.

  - A teletype sent on 15 October requests Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 19 October until 1800 Thursday, 21 October.   This is to limit pool fluctuation and reduce wear and tear on equipment.

  - A teletype sent on 18 October extends the treaty fishing outlined in the teletype sent on 15 October.  It is requested that Bonneville forebay be operated within 1.5’ band, hard constraint, for treaty fishing as follows:  0600 Tuesday, 19 October until 1800 Friday, 22 October.   This is to limit pool fluctuation and reduce wear and tear on equipment.

GLEN A. SMITH, P.E.

Operations Project Manager