### CENWP-OD-B																						28 November 2010

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 48 of 2010, which covers the period from 21 through 27 November 2010.

- OPERATION SUMMARY

  - Daily average river flows ranged from 118.5 to 140.4 kcfs.  Daily average project tailwater ranged from 11.6’ to 13.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.1’ msl.  Daily average river temperature ranged from 53 to 54ºF.  Secchi disk measurements ranged from 4.0 to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.1 to 1.2 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 1 has remained out of service since 17 September due to sticking wicket gates.

    - Unit 2 has remained out of service since 05 October for five year overhaul and U1/U2 efficiency testing.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 has remained out of service since 13 September for four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F2 has remained out of service since 15 November for annual maintenance and headgate rehab.  PH2 fishway entrances and PH2 collection channel are configured for single fish unit operation.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed to float debris from 1800 on 27 November until 0645 on 28 November.

    - FV 3-7 was closed for cleaning from 0700 until 0734 and again from 0830 until 0929 on 24 November.

    - FV 3-9 was closed for cleaning from 0705 until 0716 on 22 November, from 0700 until 0734 on 24 November, and from 1529 until 1534 on 24 November.  FV 3-9 was closed to float debris each evening from 25-28 November.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Screens scheduled to be removed after 15 December. |

  - Dewatering and Fish Salvage.

    - On 23 November, biologists removed three sturgeon and 10 sculpin from U2 tail logs.  All were released in good condition.

- RESEARCH

  - WDFW- Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 21 through 27 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/21-22 | ##### FV 3-9 picketleads | ##### Head > 0.3’ | ##### Debris | ##### Riggers cleaned on 11/22. |  |
| 11/24, 26, 27 | ##### A & B-branch, & BI weir | ##### Reading < 1.0’ | ##### FV 3-9 needs cleaning | ##### Riggers cleaned on 11/24. |  |
| 11/24-27 | ##### FV 3-9 trashrack | ##### Drawdown > 0.5’ | ##### Debris | ##### Riggers cleaned, Ops floated debris. |  |
| 11/25, 26 | ##### PH1 entrances | ##### Differential < 1.0’ | ##### FV 1-1 and 3-7 in manual | ##### Ops returned to auto 1030. |  |
| 11/25, 27 | ##### PH1 entrances | ##### Differential < 1.0’ | ##### Unknown | ##### Ops adjusted. |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| 11/26 | ##### UMT weir | ##### Reading < 1.0’ | ##### Unknown | ##### No action taken. |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 11/26, 27 | ##### PH2 south entrances | ##### Differential < 1.0’ | ##### F2 OOS | ##### Ops adjusted F1. |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. A new programmable logic controller (PLC) system has been budgeted for.

    - The PH1 PCC mechanical velocity meter remains out for maintenance crews to use as a template while constructing a new one.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 11/21 | 50.6 | 51.2 |
| 11/22 | 50.1 | 50.6 |
| 11/23 | 49.2 | 49.7 |
| 11/24 | 48.6 | 48.7 |
| 11/25 | 48.0 | 48.6 |
| 11/26 | 46.8 | 47.3 |
| 11/27 | 46.5 | 47.0 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 27 November.

    - The Washington Shore fishway entrances remain in manual due to SA-24 board calibration issues.  The operators are adjusting the gates to maintain at least a 13’ opening, as tailwater allows.

    - Stab plates were installed in 11 of 12 floating orifice gates (FOGs) on 15-17 November due to single fish unit operations.  One FOG remains out for maintenance, with a bulkhead installed in its place.

    - The Washington Shore and Cascades Island fish ladders are scheduled to go to orifice flow on 01 December, and will be dewatered to tailwater on 03 December.

    - The Bradford Island fish exit was closed for cleaning from 0705 until 0716 on 22 November.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - B2CC remains closed for the season.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chain gate 6C was closed and 7A opened on 04 August.  Chain gate 7A is set to 72’ msl.  After 01 December all chain gates will be closed except 1A, 1B, and 10B (see section BON 2.5.1.1.m. in the 2010 FPP).

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.

    - The PH2 NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain out of service for the season.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in Spring, 2011.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls within 50’ of the Cascades Island fishway resumed on 08 November.

  - BGS removal. Scheduled to begin on 06 December.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1, 10, 9, 3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.

  - A teletype sent on 19 November changes unit priority as follows: 18,15,12,17,14,1, 10,9,3,7,2,6,4,5,8, effective from 0700 until 1600 on 22 November, with a maximum of five PH2 units plus on fish unit during this time.  This operation is necessary to support removal of four node anchors upstream of the BGS.  Once this removal is complete, revert back to unit priority as specified in the teletype sent on 14 October (see 7.2).

  - A teletype sent on 19 November replaces the teletype sent on 26 October and requests the following BON tailwater elevations for chum spawning:

    - Effective immediately until further notice, hard constraint of no less than 11.3’ msl during all hours, and a hard constraint of 11.3’ to 11.7’ with a target of 11.5’, from 0630 until 1700 daily.

    - If needed, BON is authorized to pass water in excess of what is necessary to meet the 11.3’ to 11.7’ hard constraint by increasing tailwater elevation to 18.5’ msl between 1700 and 0600 hours.  Normal ramp rates apply.  It is preferred to concentrate the highest tailwater around midnight without exceeding 16.5’ msl.

    - If the actions in 7.5.2 are not sufficient, tailwater elevations may increase incrementally by 0.5’, as necessary, up to 12.5’ msl between 0600 and 1700 hours, daily.  The bottom of the range will become the new tailwater minimum.

    - The official tailwater gauge is located at river mile 144.5, on the Oregon shore.

GLEN A. SMITH, P.E.

Operations Project Manager