### CENWP-OD-B																						31 January 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 04 of 2011, which covers the period from 23 through 29 January 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 232.2 to 277.8 kcfs.  Daily average project tailwater ranged from 19.9’ to 22.5’ msl.  Daily average powerhouse forebay elevation ranged from 71.5’ to 72.4’ msl.  Daily average river temperature ranged from 38 to 40ºF.  Secchi disk measurements ranged from 2.3 to 4.0’.

  - Spill Bay 18, which provides attraction flow for B-branch, is open 6” during daylight hours.  Daily average spill ranged from 1.4 to 37.7 kcfs.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 1 has remained out of service since 17 September due to sticking wicket gates.

    - Unit 3 was out of service from 1309 until 1631 on 26 January to rake trash.

    - Unit 9 was out of service from 0301 on 24 January until 1438 on 25 January for a 100 day inspection.

    - Unit 10 was out of service from 0819 until 1318 on 27 January to rake trash.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 18 was out of service from 0803 until 1218 on 26 January for cooling water strainer inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 and F2 remain out of service while the WS fishway is dewatered.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 3-7 was closed for cleaning from 0719 until 0739 on 25 January and from 0720 until 0918 on 26 January.

    - FV 3-9 was closed for cleaning from 0727 until 0739 on 24 January and from 0720 until 0918 on 26 January.

    - FV 5-3, 5-4, and 5-9 remain closed while the Cascades Island fishway is dewatered.

    - FV 6-9 remains closed while the WS fishway is dewatered.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | STSs scheduled to be reinstalled the week of 22 February. |

  - Dewatering and Fish Salvage.  The following fish salvage activities occurred this week:

    - From 25-28 January, Project Fisheries, with assistance from Project Maintenance crews and Fish Field Unit, recovered approximately 1600-1700 sturgeon, two steelhead, and two sculpin from the PH2 collection channel north of U12 and the north monolith.  All fish were released to the tailrace near the NUE in good condition.  Some sturgeon had minor scrapes. Some sea lion predation was observed in the vicinity of the released sturgeon at the end of the day on 26 January so an ODFW sea lion hazer was on site to keep predation at a minimum for the remainder of the fish salvage.

- RESEARCH

  - FFU - Sea lion.  Observations began on 07 January.

  - ODFW - Sea lion hazing.  Hazing from the deck occurred on 27 January.

  - ODFW - Sea lion trapping. Moved sea lion traps adjacent to the B2CC and downstream of the old Navlock on 27 January.  Trapping has not begun for the season.

  - WDFW - Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 24, 25, and 28 January.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |  | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |  |
| 01/24 | FV 4-3 | Drawdown > 0.5’ | Debris |  | None |  |  |
| CASCADES ISLAND (CI) – Dewatered |  |  |  |  |  |  |  |
| WASHINGTON SHORE (WS) – Dewatered |  |  |  |  |  |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The PH1 PCC mechanical velocity meter remains out for maintenance crews to use as a template while constructing a new one.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 28 January.

    - The Washington Shore and Cascades Island fish ladders remain dewatered.

    - Stab plates or bulkheads remain installed in the floating orifice gates (FOGs) while the WS fishway remains dewatered. One FOG remains out for maintenance.

    - SLEDs remain at PH1 and B-branch entrances.

    - The Bradford Island fish ladder exit was closed for cleaning from 0720 until 0745 on 26 January.

  - Juvenile Fishways.

    - DSM2 remains dewatered for winter maintenance.

    - B2CC remains closed for the season.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Chaingates 1A, 1B, and 10B remain open. Chaingates 2B, 4A, and 7A were opened on 22 January to assist in floating trash.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir and slot filler remain installed.  Cascade Is. LPS remains out of service for the season.

    - The PH2 NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain out of service for the season.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in June, 2011.

  - Spillway Gate Repair Pit. Clean-up of hazardous material is complete.  Shoring of the walls continues.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 16 July 2009, changes PH2 unit priority to: 12,18,15,17,14,13,16.  This change is effective from 1100 on 16 July 2009 until U11 returns to service.

  - A teletype sent on 14 October requests BON project change PH1 unit priority as follows: 1,10,9,3,7,2,6,4,5,8, effective immediately until further notice. This moves Unit 9 to third in priority, and replaces the teletype sent on 29 July that moved Unit 7 to third in priority. This operation is necessary to complete a 100 day operation per PH1 rehab contract.

  - A teletype sent on 22 December outlines new tailwater operations for chum incubation.  Effective immediately, BON is requested to maintain a tailwater of 12.2’ or greater for all hours.

  - A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7).

GLEN A. SMITH, P.E.

Operations Project Manager