### CENWP-OD-B																						20 March 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 11 of 2011, which covers the period from 13 through 19 March 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 202.3 to 245.9 kcfs.  Daily average project tailwater ranged from 18.1’ to 20.6’ msl.  Daily average powerhouse forebay elevation ranged from 72.7’ to 73.6’ msl.  Daily average river temperature ranged from 40 to 41ºF.  Secchi disk measurements ranged from 4.0 to 5.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 1 was out of service from 1608 until 1738 on 17 March and from 0830 until 1054 on 18 March to rake trash.

    - Unit 2 was out of service from 1330 until 1605 on 17 March to rake trash.

    - Unit 3 was out of service from 1058 until 1335 on 18 March to rake trash.

    - Unit 4 was out of service from 1337 until 1519 on 18 March and from 0713 until 0817 on 19 March to rake trash.

    - Unit 5 was out of service from 0819 until 1046 on 19 March to rake trash.

    - Unit 6 was out of service from 1048 until 1348 on 19 March to rake trash.

    - Unit 7 was out of service from 1351 until 1612 on 19 March to rake trash.

    - Unit 8 was out of service from 1615 until 1700 on 19 March to rake trash.

    - Unit 9 was out of service from 1411 until 1546 on 15 March to rake trash.

    - Unit 10 was out of service from 1102 until 1409 on 15 March to rake trash.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 1513 until 1611 on 16 March to rake trash.

    - Unit 13 was out of service from 1616 until 1654 on 16 March and from 0721 until 0802 on 17 March to rake trash.

    - Unit 14 was out of service from 0806 until 0839 on 17 March to rake trash.

    - Unit 15 was out of service from 0843 until 1014 on 17 March to rake trash.

    - Unit 16 was out of service from 1021 until 1107 on 17 March to rake trash.

    - Unit 17 was out of service from 1114 until 1149 on 17 March to rake trash.

    - Unit 18 was out of service from 1236 until 1327 on 17 March to rake trash.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 1-1 was closed for cleaning from 0906 until 0918 on 17 March and from 0755 until 0811 on 18 March.

    - FV 3-7 was closed for cleaning from 0728 until 0844 on 17 March.

    - FV 3-9 was closed for cleaning from 0714 until 0728 on 14 March and from 0731 until 0746 on 18 March.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 04 April |

  - Dewatering and Fish Salvage.  No fish salvage activities occurred this week:

- RESEARCH

  - Battelle - survival study.  Acoustic tag training began the week of 07 March.  Fish for training currently held in raceways at the SMF.  Hydrophone installation began this week.

  - CRITFC - Sea lion hazing.  Hazing from boats continues.

  - FFU - Sea lion.  Observations continue.

  - NOAA - lamprey. DIDSON mount installed on the NDE LPS on 15 February.

  - ODFW/WDFW - Sea lion trapping. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Trapping has not begun for the season.

  - PSMFC.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  27 steelhead.  Please see http://www.fpc.org/adultsalmon/bonkeltcounts.htm for updated kelt counts.

  - WDFW - Fish Counting.  Video counting continues.

  - USDA - Sea lion hazing. Hazing from the deck continues.

- FISHWAYS

  - Project biologists inspected 13 through 19 March.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 3/18-19 | PH1CC south entrance | Differential < 1.0’ | Unknown | Operations adjusted. |  |
| CASCADES ISLAND (CI) – nothing to report |  |  |  |  |  |
| 3/16 | UMT staff gauge | < 1.0’ | Unknown | No action taken. |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 3/13 | PH2 entrances | < 13’ opening | In manual | Operations adjusted. |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The PH1 PCC mechanical velocity meter has been repaired and a new mechanical velocity meter has been fabricated for PH2. Both are scheduled for installation.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 3/13 | 39.5 | 39.9 |
| 3/14 | 39.6 | 40.0 |
| 3/15 | 39.8 | 40.2 |
| 3/16 | 40.2 | 40.6 |
| 3/17 | 40.3 | 40.8 |
| 3/18 | 40.4 | 40.9 |
| 3/19 | 40.5 | 41.0 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 19 March. Weir gates 2 and 64 need recalibration. TR #11-113806 submitted.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs remain installed at all fishway entrances.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open. Automated chaingates 3B, 6C, and 10B are open and functioning in manual. The electrical problem preventing automatic operation is being addressed.

    - The hydrocannon remains in service.

    - The Kelt trigger was reached on 13 March (see section BON 2.4.2.3.a. in the 2011 FPP). The B2CC opened at 1402 on 14 March.

    - The B2CC was closed from 0744 until 1014 on 16 March to facilitate debris removal jammed behind a trolley pipe just outside the B2CC entrance.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  Cascade Is. LPS remains out of service.

    - The NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain out of service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in June, 2011.

  - Spillway Gate Repair Pit. Clean-up of hazardous material and shoring of the walls is complete.  Load test scheduled to occur spring 2011.

  - B2CC Hoist. Construction scheduled to begin fall of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December outlines new tailwater operations for chum incubation.  Effective immediately, BON is requested to maintain a tailwater of 12.2’ or greater for all hours.

  - A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7).

  - A teletype sent on 14 March authorizes BON to open the corner collector (B2CC). If TDG at the Warrendale site exceeds 105% after 24 hours of operation, close Spillbays 1 and 18.  If the 105% TDG is still exceeded after 24 hours operating without spillbays, then close the B2CC and operate PH1 as the priority powerhouse.

  - A teletype sent on 15 March changes the TDG exceedance from 105% to 110% in the above teletype (see 7.3). All other aspects of the above teletype remain the same.

  - A teletype sent on 15 March requests a short term closure of the B2CC on 16 March from 0700 to 1200 hours to remove debris from the entrance.

GLEN A. SMITH, P.E.

Operations Project Manager