### CENWP-OD-B																						15 May 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 19 of 2011, which covers the period from 08 through 14 May 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 252.5 to 358.8 kcfs.  Daily average project tailwater ranged from 20.2’ to 25.8’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 74.6’ msl.  Daily average river temperature ranged from 51 to 52ºF.  Secchi disk measurements ranged from 3.0’ to 3.5’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 99.5 to 129.2 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS valves were closed this reporting week.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 06 June. |

  - Dewatering and Fish Salvage.  No fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle - survival study.  Acoustic tagging and fish releases continue.

  - CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CRITFC - Sea lion hazing.  Hazing from boats continues.  Acoustic receivers for sea lion tags anchored in BRZ.  Video camera system for sea lion observation set up at PH2 south monolith.

  - FFU - Sea lion.  Observations continue.  Weekly pinniped reports can be found at

http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2011/sea_lion_hazing2011.html

  - Kintama Research.  Acoustic tagging yearling Chinook at the SMF continues.  No research fish collected this week.

  - NOAA - COE Walla Walla District transportation evaluation.  Sort by Code collections at the SMF continue.

  - NOAA - lamprey. DIDSON mount installed on the NDE LPS on 15 February.  LPS count network remains installed.

  - ODFW/WDFW - Sea lion trapping. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Acoustic tagging and branding continues.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  70 steelhead, 34 salmon and 24 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.  A total of 50 yearling Chinook and 50 coho were collected for NOAA research this week.

  - WDFW - Fish Counting.  Visual counting continues.

  - USDA - Sea lion and avian hazing. Hazing from the deck continues.

- FISHWAYS

  - Project biologists inspected 08 through 14 May.

  - Fish Passage Plan Observations.

- Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 5/10 | PH1 North entrance | Differential > 2.0’ | Unknown | Calibration issues. | 11-150329 |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| 5/9 | UMT staff gauge | Reading < 0.9’ | Unknown | Operations adjusted. |  |
| WASHINGTON SHORE (WS) – Nothing to report. |  |  |  |  |  |
| 5/14 | PH2 diffusers | Incorrect position | System in manual | Operations adjusted |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - The PH1 PCC mechanical velocity meter has been repaired and was installed on 12 May. A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 5/8 | 49.9 | 50.4 |
| 5/9 | 50.1 | 50.6 |
| 5/10 | 50.8 | 51.3 |
| 5/11 | 51.2 | 51.7 |
| 5/12 | 51.6 | 52.0 |
| 5/13 | 52.0 | 52.4 |
| 5/14 | 52.4 | 52.8 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 14 May.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs remain installed at all fishway entrances.

    - The AFF remains watered up.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC remains in service.  One avian line remains broken.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  The CI LPS remains out of service.

    - The NDE ramp remains in the lowered position and is not currently operating.

    - Bradford Island and WA Shore LPS’s remain out of service.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in August, 2011.

  - Spillway Gate Repair Pit. Clean-up of hazardous material and shoring of the walls is complete.  Load test scheduled to occur spring 2011.

  - B2CC Hoist. Construction scheduled to begin fall of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December notifies BON that slow roll start-up for units that have been idle for 12 hours or more is required from 01 December through 30 April (see FPP section BON 5.7).  Note: Though specified in the FPP and the teletype as only occurring when units have been idle for 12 or more hours, Bonneville has been starting all idle units with slow roll protocol.

  - A teletype sent on 08 April requests spill for juvenile fish passage begin at 0001 hours on Sunday, 10 April and continue through 20 June at 2400 hours. Spill approximately 100 kcfs 24 hours a day using the spill pattern in the 2011 FPP.  If Bonneville inflows are too low to maintain the 100 kcfs spill and minimum turbine discharge of 30-40 kcfs, then operate to minimum discharge and spill to pass inflow.

  - A teletype sent on 27 April requests special operations for the Spring Creek hatchery. Beginning 1800 on 04 May until 1700 on 08 May as a hard constraint, and from 1700 on 08 May until 1700 on 12 May as a soft constraint, operate PH2 units at the 25% range of the 1% limit. The timing of this operation may be altered if requested by a BON Project Biologist. If additional generation is and PH1 is fully loaded, increase generation at PH2 one at a time to 50% of the 1% limit and then to 100% of the 1% limit.

  - A teletype sent on 03 May requests that BON forebay be maintained between elevation 72.0-73.0’ as a soft constraint from 0800 to 1200 hours Saturday 07 May, for beach clean up at Hood River.

GLEN A. SMITH, P.E.

Operations Project Manager